## Slide 1: W_N Stability Limit update
10/09/2012
ERCOT Operations to Congestion management Working Group
Bill Blevins
Manager Operations Support

## Slide 2: Limit calculation
ERCOT Operations Engineering calculates the limits that are used in DAM and RUC
Using SMTNET 24 basecases are created for each day.
Limits are calculated using Load forecast, Outages from the outage scheduler and a generation pattern for the expected load.
Using DSA manager limits are calculated using VSAT and TSAT.
VSAT and TSAT are third party software that is integrated into the Alstom EMS. VSAT and TSAT increase the transfer by scaling load or generation in specific areas across a cut plane.
Contingencies are simulated and if the system s determined to be unstable then the limit is established. This process is repeated until the software finds a limit.
Limits are then generated by the system for all 24 hours. They are then adjusted by a 90% discount factor the operators use to control the limit in real-time.
These limits are passed to DAM and RUC and also posted to the MIS.
These limits are established typically 2 days ahead so that they can be used in the DAM and DRUC. They are also run in real-time.
ERCOT Operations
10/09/2012

## Slide 3: Cut Plane for the W_N Stability interface
ERCOT Operations
10/09/2012

## Slide 4: Why are the interfaces being changed?
ERCOT Operations
10/09/2012

## Slide 5: Summary
New limit will be used after the CREZ lines (BWNSW to KLNSW) go in service (planned 12/15).
We also received the new WN matrix from our planning study group. This will be retired once the Wind Model project for TSAT is complete.
We believe once we have the wind models in TSAT we will be able to use TSAT to monitor dynamic voltage stability conditions in the west, which will retire the WN matrix.
The TSAT wind model project is supposed to be finished around May next year.
The cut plane should not change any generators locations.
However, the shift factors on WN interface will change after those two lines go in service, mostly on the north side.
ERCOT will send a market notice out before using the new planning matrix in the DAM detailing the location of this matrix.
ERCOT Operations
10/09/2012