## Purpose
| 2/23/2023 11/16/2023 | ERCOT Public
Mapping Document Related to NERC Reliability Standards IRO-010-3-4 & TOP-003-4-5
Purpose
ERCOT ISO maintains this mapping document as required by North American Electric Reliability Corporation (NERC) Reliability Standards IRO-010-3-4 and TOP-003-4-5. This mapping document provides applicable NERC-registered entities with a list of existing Protocol and Operating Guide references that identify the data, specifications and other relevant information required by ERCOT ISO to build and maintain its models to support Real-time Monitoring, Operational Analyses, and Real-time assessments. The periodicity for providing data, data formats, processes for resolving data conflicts, and security protocols, where applicable, are detailed within the language of the Protocols, Operating Guides, and other binding documents for their respective data specification. ERCOT ISO and the NERC-registered entities collectively coordinate revisions to the Protocols, Operating Guides, and Other Binding Documents in a mutually agreeable manner by way of the ERCOT regional stakeholder processes. In the event of a conflict between the Protocols, Operating Guides, or ICCP Communications Handbook and this mapping document, the Protocols and Other Binding Documents prevail.
Revision and Distribution Process
This mapping document will be maintained by ERCOT ISO. Substantive revisions will be distributed via market notice and posted to the ERCOT website.

## Data Requirements
Data Required for OPA, RTA, & Real Time Monitoring
Section | Protocol Language | OPA | RTA | RTM | Periodicity | Deadline | Format & Security Protocol
3.1.4.4 | Management of Forced Outages or Maintenance Outages | Header | Header | Header
3.1.4.4(3) | For Maintenance Outages, the Resource Entity or QSE, as appropriate, or TSP shall notify ERCOT of any Resource or Transmission Facilities Maintenance Outage according to the Maintenance Outage Levels by updating the COP and Outage Scheduler. ERCOT shall coordinate the removal of facilities from service within the defined timeframes as specified by the TSP, QSE or Resource Entity in its notice to ERCOT. | X |  |  | Continually | See timing tables in 3.1.5.3 (1), 3.1.6.6 (1) & 3.1.7.1 (2) | Outage Scheduler Encrypted via https; authenticated via Digital Certificate
3.1.4.5 | Notice of Forced Outage or Unavoidable Extension of Planned Maintenance Outage, or Rescheduled Due to Unforeseen Events | Header | Header | Header
3.1.4.5(1) | If a Planned, Maintenance, or Rescheduled Outage is not completed within the ERCOT-approved timeframe and the Transmission Facilities or Resources are in such a condition that they cannot be restored at the Outage schedule completion date, the requesting party shall submit to ERCOT a Forced Outage (unavoidable extension) form describing the extension of the Outage and providing a revised return date. | X |  |  | As it occurs | Before Planned, Maintenance or Rescheduled outages ends | Outage Scheduler Encrypted via https; authenticated via Digital Certificate
3.1.4.5(2) | Any transmission Forced Outage that occurs in Real-Time and that is expected to continue for longer than two hours must be entered into the Outage Scheduler as soon as practicable but no longer than 60 minutes after the beginning of the Outage. Any transmission Forced Outage with a duration exceeding two hours must be entered into the Outage Scheduler as soon as practicable but no longer than 150 minutes after the beginning of the transmission Forced Outage, if not already reported in the Outage Scheduler. | X |  |  | As it occurs | If outage remains longer than two hours | Outage Scheduler Encrypted via https; authenticated via Digital Certificate
3.1.4.5(3) | Any Resource Forced Outage that occurs in Real-Time must be entered into the Outage Scheduler as soon as practicable but no longer than 60 minutes after the beginning of the Forced Outage. | X |  |  | As it occurs | No longer than 60 minutes after the beginning of the Forced Outage | Outage Scheduler Encrypted via https; authenticated via Digital Certificate
3.1.4.5(5) | For a Startup Loading Failure, the Resource Entity or its designee must enter a Forced Outage in the Outage Scheduler if the Resource was in an Off-Line status prior to the Startup Loading Failure or update the existing Outage for the Resource if the Resource was on Outage prior to the Startup Loading Failure. The Resource Entity or its designee must also provide a text entry in the supporting information field of the Outage Scheduler that includes the following: (a) A statement that a Startup Loading Failure occurred; (b) An explanation of the cause of the Startup Loading Failure using the best available information at the time the Outage or update to the existing Outage is entered, which must be updated if more accurate information becomes available; and (c) The start time and end time of the Startup Loading Failure portion of the Outage. Multiple consecutive startup attempts may be aggregated into a single Startup Loading Failure event with a single start and end time. | X |  |  | As it occurs | No longer than 60 minutes after the beginning of the Forced Outage | Outage Scheduler Encrypted via https; authenticated via Digital Certificate
3.1.4.7 | Reporting of Forced Derates | Header | Header | Header
3.1.4.7(1) | If a Generation Resource experiences a Forced Derate in an amount greater than ten MW, and 5% of its Seasonal net maximum sustainable rating, and the Forced Derate lasts longer than 30 minutes, the Resource Entity or its designee must enter the Forced Derate into the Outage Scheduler as soon as practicable but no longer than 60 minutes after the beginning of the Forced Derate. | X |  |  | As it occurs | No longer than 60 minutes after the beginning of the Forced Derate | Outage Scheduler Encrypted via https; authenticated via Digital Certificate
3.1.4.7(2) | If a Forced Derate that has already been reported changes by an amount greater than ten MW and 5% of the Generation Resource’s Seasonal net maximum sustainable rating, and the change lasts longer than 30 minutes, the Resource Entity or its designee must enter the change as a new Forced Derate into the Outage Scheduler as soon as practicable but no longer than 60 minutes after the beginning of the change. | X |  |  | As it occurs | No longer than 60 minutes after the beginning of the change | Outage Scheduler Encrypted via https; authenticated via Digital Certificate
3.1.4.7(3) | Notwithstanding paragraphs (1) and (2) above, for any Forced Derate or change to a Forced Derate that meets the reporting criteria specified in paragraph (1) or (2) above and that is caused by ambient temperature or humidity, the Resource Entity or its designee must enter the Forced Derate into the Outage Scheduler as soon as practicable but no longer than eight hours after the beginning of the Force Derate or change. | X |  |  | As it occurs | No longer than 8 hours after the beginning of the Forced Derate or change | Outage Scheduler Encrypted via https; authenticated via Digital Certificate
3.1.4.7(4) | The QSE must appropriately update the telemetered High Sustained Limit (HSL) and any applicable telemetry as specified in paragraph (2) of Section 6.5.5.2, Operational Data Requirements, based on the Forced Derate, as soon as practicable but no longer than 15 minutes after the beginning of a Forced Derate, if the Forced Derate is greater than ten MW and more than 5% of the Seasonal net maximum sustainable rating of the Resource and its expected or actual duration is greater than 30 minutes. Alternatively for a Forced Derate, a QSE may use the ONHOLD process described in paragraph (2) of Section 6.5.5.1, Changes in Resource Status. |  | X | X | As it occurs | As soon as reasonably practicable but no longer than 15 minutes after the Forced Derate occurs | ICCP naming convention Private WAN point-to-point connection (RTA)
3.1.4.7(5) | The QSE must update the COP as soon as practicable but no longer than 60 minutes after the beginning of a Forced Derate, if the Forced Derate is greater than 20 MW and its expected duration is greater than 120 minutes. | X |  |  | As it occurs | No longer than 60 minutes after the beginning of a Forced Derate | Outage Scheduler Encrypted via https; authenticated via Digital Certificate
3.1.4.7(6) | Each QSE shall timely update the telemetered HSL and COP unless in the reasonable judgment of the QSE, such compliance would create an undue threat to safety, undue risk of bodily harm, or undue damage to equipment. The QSE is excused from updating the telemetered HSL and/or COP only for so long as the undue threat to safety, undue risk of bodily harm, or undue damage to equipment exists. The time for updating the telemetered HSL and/or COP begins once the undue threat to safety, undue risk of bodily harm, or undue damage to equipment no longer exists. | X | X | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA)
3.1.5.1 | ERCOT Evaluation of Planned Outage and Maintenance Outage of Transmission Facilities
3.1.5.1(1) | A TSP or Resource Entity shall request a Planned Outage or Maintenance Outage when any Transmission Facility that is part of the ERCOT Transmission Grid and defined in the Network Operations Model will be removed from its normal service. For Resource Entities within a Private Use Network, this only includes Transmission Facilities at the Point of Interconnection (POI). For TSP requests, the TSPs shall enter such requests in the Outage Scheduler. For Resource Entity requests, the Resource Entity shall enter such requests in the Outage Scheduler. Planned Outages, Maintenance Outages, or Rescheduled Outages for Electrical Buses will be treated as consequentially outaged Transmission Elements. In those cases where a TSP enters the breaker and switch statuses associated with an Electrical Bus, a downstream topology processor will evaluate the breakers and switches associated with the applicable Electrical Bus to determine if the Electrical Bus is consequentially outaged, and to thereby designate the status of the Electrical Bus. Proposed Transmission Planned Outage or Maintenance Outage information submitted by a TSP or Resource Entity in accordance with this Section constitutes a request for ERCOT’s approval of the Outage Schedule associated with the Planned Outage or Maintenance Outage. ERCOT is not deemed to have approved the Outage Schedule associated with the Planned Outage or Maintenance Outage until ERCOT notifies the TSP or Resource Entity of its approval under procedures adopted by ERCOT. ERCOT shall evaluate requests under Section 3.1.5.11, Evaluation of Transmission Facilities Planned Outage or Maintenance Outage Requests. | X |  |  | As it occurs | See timing table | Outage Scheduler Encrypted via https; authenticated via Digital Certificate
3.1.5.12 | Submittal Timeline for Transmission Facility Outage Requests | Header | Header | Header
3.1.5.12(1) | TSPs shall submit all requests for Planned Outages and Maintenance Outages or changes to existing approved Outages of Transmission Elements in the Network Operations Model to ERCOT no later than the minimum amount of time between the submittal of a request to ERCOT for approval of a proposed Outage and the scheduled start date of the proposed Outage, according to the following table. | X |  |  | Continually | See timing table | Outage Scheduler Encrypted via https; authenticated Digital Certificate
3.1.6.2 | Resources Outage Plan | Header | Header | Header
3.1.6.2(1) | Resource Outage plans shall include the following information: | Intro | Intro | Intro
3.1.6.2(1)(a) | The primary and alternate phone number of the Resource Entity’s Single Point of Contact for Outage Coordination; | X |  |  | As known | 45 days or immediately | Outage Scheduler Encrypted via https; authenticated Digital Certificate
3.1.6.2(1)(b) | The Resource identified by the name in the Network Operations Model; | X |  |  | As known | 45 days or immediately | Outage Scheduler Encrypted via https; authenticated Digital Certificate
3.1.6.2(1)(c) | The net megawatts of capacity the Resource Entity anticipates will be available during the Outage (if any); | X |  |  | As known | 45 days or immediately | Outage Scheduler Encrypted via https; authenticated Digital Certificate
3.1.6.2(1)(d) | The estimated start and finish dates for each Planned and Maintenance Outage; | X |  |  | As known | 45 days or immediately | Outage Scheduler Encrypted via https; authenticated Digital Certificate
3.1.6.2(1)(e) | An estimate of the acceptable deviation in the Outage schedule (i.e., the earliest start date and the latest finish date for the Outage); and | X |  |  | As known | 45 days or immediately | Outage Scheduler Encrypted via https; authenticated Digital Certificate
3.1.6.2(1)(f) | The nature of work to be performed during the Outage. For a Forced Outage or Forced Derate, the “nature of work” field in the Outage Scheduler shall indicate the best available information about the cause of the Forced Outage or Forced Derate at the time the Outage or derate is entered and shall be updated as soon as more accurate information becomes available. | X |  |  | As known | 45 days or immediately | Outage Scheduler Encrypted via https; authenticated Digital Certificate
3.1.6.11 | Outage Returning Early | Header | Header | Header
3.1.6.11(1) | A Resource that completes a Planned Outage early and wants to resume operation shall notify ERCOT of the early return prior to resuming service by making appropriate entries in the Current Operating Plan COP or Outage Scheduler if applicable as much in advance as practicable, but not later than at least two hours prior to beginning startup. Within two hours of receiving such request, ERCOT shall either: | X |  |  | As known | No later than 2 hours before start up | Outage Scheduler Encrypted via https; authenticated Digital Certificate
3.6.1 | Load Resource Participation | Header | Header | Header
3.6.1(1) | A Load Resource may participate by providing: | Intro | Intro | Intro
3.6.1(1)(a) | Ancillary Service: | Intro | Intro | Intro
3.6.1(1)(a)(i) | Regulation Up (Reg-Up) Service as a Controllable Load Resource capable of providing Primary Frequency Response; |  |  | X | 2 seconds | Continuous | ICCP naming convention Private WAN point-to-point connection
3.6.1(1)(a)(ii) | Regulation Down (Reg-Down) Service as a Controllable Load Resource capable of providing Primary Frequency Response; |  |  | X | 2 seconds | Continuous | ICCP naming convention Private WAN point-to-point connection
3.6.1(1)(a)(iii) | Responsive Reserve (RRS) as a Controllable Load Resource qualified for Security-Constrained Economic Dispatch (SCED) Dispatch and capable of providing Primary Frequency Response, or as a Load Resource controlled by high-set under-frequency relay; |  |  | X | 2 seconds | Continuous | ICCP naming convention Private WAN point-to-point connection
3.6.1(1)(a)(iv) | ERCOT Contingency Reserve Service (ECRS) as a Controllable Load Resource qualified for SCED Dispatch and capable of providing Primary Frequency Response, or as a Load Resource that may or may not be controlled by high-set under-frequency relay; |  |  | X | 2 seconds | Continuous | ICCP naming convention Private WAN point-to-point connection
3.6.1(1)(a)(iv)(v) | Non-Spinning Reserve (Non-Spin) as a Controllable Load Resource qualified for SCED Dispatch or as a Load Resource that is not a Controllable Load Resource and that is not controlled by under-frequency relay; and |  |  | X | 2 seconds | Continuous | ICCP naming convention Private WAN point-to-point connection
3.6.1(1)(a)(v)(vi) | A Load Resource that is not a Controllable Load Resource cannot simultaneously provide Non-Spin and RRS in Real-Time; |  |  | X | 2 seconds | Continuous | ICCP naming convention Private WAN point-to-point connection
3.6.1(1)(b) | Energy in the form of Demand response from a Controllable Load Resource in Real-Time via SCED; |  |  | X | 2 seconds | Continuous | ICCP naming convention Private WAN point-to-point connection
3.6.1(1)(c) | Emergency Response Service (ERS) for hours in which the Load Resource does not have an Ancillary Service Resource Responsibility; and |  |  | X | 2 seconds | Continuous | ICCP naming convention Private WAN point-to-point connection
3.6.1(1)(d) | Voluntary Load response in Real-Time. |  |  | X | 2 seconds | Continuous | ICCP naming convention Private WAN point-to-point connection
3.7 | Resource Parameters | Header | Header | Header
3.7(1) | A Resource Entity shall register Generation Resources, Settlement Only Generators (SOGs), and Load Resources pursuant to Planning Guide Section 6.8, Resource Registration Procedures. The Resource Parameters, listed in Section 3.7.1, Resource Parameter Criteria, are a subset of Resource Registration data defined in the Resource Registration Glossary. | X |  |  | As needed | Model ready date | Resource Registration Encrypted via https; authenticated via Digital Certificate
3.7.1.1 | Generation Resource Parameters | Header | Header | Header
3.7.1.1 (1) | Generation Resource Parameters that may be modified, with documented reason for change, by the QSE for immediate use upon ERCOT validation include: | Intro | Intro | Intro
3.7.1.1 (1)(a) | Normal Ramp Rate curve; | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate
3.7.1.1 (1)(b) | Emergency Ramp Rate curve; | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate
3.7.1.1 (1)(c) | Minimum On-Line time; | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate
3.7.1.1 (1)(d) | Minimum Off-Line time; | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate
3.7.1.1 (1)(e) | Maximum On-Line time; | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate
3.7.1.1 (1)(f) | Maximum daily starts; | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate
3.7.1.1 (1)(g) | Maximum weekly starts; | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate
3.7.1.1 (1)(h) | Maximum weekly energy; | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate
3.7.1.1 (1)(i) | Hot start time; | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate
3.7.1.1 (1)(j) | Intermediate start time; | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate
3.7.1.1 (1)(k) | Cold start time; | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate
3.7.1.1 (1)(l) | Hot to intermediate time; and | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate
3.7.1.1 (1)(m) | Intermediate to cold time. | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate
3.7.1.2 | Load Resource Parameters | Header | Header | Header
3.7.1.2(1) | Resource Parameters that may be modified, with documented reason for change, by the QSE for immediate use upon ERCOT validation, which may be adjusted to reflect Distribution Losses in accordance with Section 8.1.1.2, General Capacity Testing Requirements, include the following for each of its Load Resources that is a non-Controllable Load Resource: | Intro | Intro | Intro
3.7.1.2(1)(a) | Maximum interruption time; | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate
3.7.1.2(1)(b) | Maximum daily deployments; | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate
3.7.1.2(1)(c) | Maximum weekly deployments; | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate
3.7.1.2(1)(d) | Maximum weekly energy; | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate
3.7.1.2(1)(e) | Minimum notice time; | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate
3.7.1.2(1)(f) | Minimum interruption time; and | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate
3.7.1.2(1)(g) | Minimum restoration time. | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate
3.7.1.2(2) | Resource Parameters that may be modified, with documented reason for change, by the QSE for immediate use upon ERCOT validation, which may be adjusted to reflect Distribution Losses in accordance with Section 8.1.1.2, include the following for each of its Controllable Load Resources, including Aggregate Load Resources (ALRs): | Intro | Intro | Intro
3.7.1.2(2)(a) | Normal Ramp Rate curve; | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate
3.7.1.2(2)(b) | Emergency Ramp Rate curve; | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate
3.7.1.2(2)(c) | Maximum deployment time; and | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate
3.7.1.2(2)(d) | Maximum weekly energy. | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate
3.8.3 | Quick Start Generation Resources | Header | Header | Header
3.8.3(1) | The QSE for a Quick Start Generation Resource (QSGR) that is available for deployment by SCED shall set the COP Resource Status to OFFQS, and the COP Low Sustained Limit (LSL) and COP HSL values to the expected sustainable LSL and HSL for the QSGR for the hour. If the QSGR is providing Non-Spinning Reserve (Non-Spin) service, then the Ancillary Service Resource Responsibility for Non-Spin shall be set to the Resource’s QSE-assigned Non-Spin responsibility in the COP. If the QSGR is providing ERCOT Contingency Reserve Service (ECRS), then the Ancillary Service Resource Responsibility for ECRS shall be set to the Resource’s QSE-assigned ECRS responsibility in the COP. | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate
3.8.3(2) | The QSGR that is available for deployment by SCED shall telemeter a Resource Status of OFFQS and a LSL of zero prior to receiving a deployment instruction from SCED. This status is necessary in order for SCED to recognize that the Resource can be Dispatched. The status of the breaker shall be open and the output of the Resource shall be zero in order for the State Estimator to correctly assess the state of the system. After being deployed for energy from SCED, the Resource shall telemeter an LSL equal to or less than the Resource’s actual output until the Resource has ramped to its physical LSL. After reaching its physical LSL, the QSGR shall telemeter an LSL that reflects its physical LSL. The QSGR that is providing Off-Line Non-Spin shall always telemeter an Ancillary Service Resource Responsibility for Non-Spin to reflect the Resource’s Non-Spin obligation and shall always telemeter an Ancillary Service Schedule for Non-Spin of zero to make the capacity available for SCED. |  | X | X | 2 seconds | Continuous | ICCP naming convention Private WAN point-to-point connection
3.8.3(5) | For a QSGR that is physically Off-Line, the Resource Entity shall submit a Normal Ramp Rate curve and Emergency Ramp Rate curve indicating QSGR’s ability to reach its ten-minute tested output from zero output in five minutes. This is necessary to prevent SCED from deploying multiple QSGRs due to ramp limitation in the first five minutes after being Dispatched by SCED. | X |  |  | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate
3.9 | Current Operating Plan (COP) | Header | Header | Header
3.9 (9) | When ERCOT issues a communication in the form of an Operating Condition Notice (OCN), Advisory, Watch, or Emergency Notice due to forecasted or actual cold or hot weather, for each Generation Resource and Energy Storage Resource (ESR) a QSE represents, the QSE shall update the COP, Real-Time telemetry, and Outage or derate reporting to reflect any Resource-specific operating limitations based on: (i) capability and availability; (ii) fuel supply or inventory concerns, including fuel switching capabilities; or (iii) environmental constraints and the impact on the Generation Resource or ESR due to the weather conditions. QSEs shall provide these updates in accordance with Sections 3.1.4, Communications Regarding Resource and Transmission Facility Outages; 3.10.7.5, Telemetry Requirements; 3.9, Current Operating Plan (COP); 3.9.1, Current Operating Plan (COP) Criteria; and Nodal Operating Guide Section 7.3, Telemetry. | X | X | X | As needed | As needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) ICCP Naming Convention Private WAN point-to-point connection (RTA)
3.9.1 | Current Operating Plan (COP) Criteria | Header | Header | Header
3.9.1(2) | Each QSE that represents a Resource shall update its COP reflecting changes in availability of any Resource as soon as reasonably practicable, but in no event later than 60 minutes after the event that caused the change. Each QSE shall timely update its COP unless in the reasonable judgment of the QSE, such compliance would create an undue threat to safety, undue risk of bodily harm, or undue damage to equipment. The QSE is excused from updating the COP only for so long as the undue threat to safety, undue risk of bodily harm, or undue damage to equipment exists. The time for updating the COP begins once the undue threat to safety, undue risk of bodily harm, or undue damage to equipment no longer exists. | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate
3.9.1(5) | A COP must include the following for each Resource represented by the QSE: | Intro | Intro | Intro
3.9.1(5)(a) | The name of the Resource; | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate
3.9.1(5)(b) | The expected Resource Status: | X |  |  | As soon as reasonably practicable | No later than 60 minutes after the event | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate
3.9.1(5)(b)(i) | Select one of the following for Generation Resources synchronized to the ERCOT System that best describes the Resource’s status. Unless otherwise provided below, these Resource Statuses are to be used for COP and/or Real-Time telemetry purposes, as appropriate. | Intro | Intro | Intro
3.9.1(5)(b)(i)(A) | ONRUC – On-Line and the hour is a RUC-Committed Hour; | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA)
3.9.1(5)(b)(i)(B) | ONREG – On-Line Resource with Energy Offer Curve providing Regulation Service; | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA)
3.9.1(5)(b)(i)(C) | ON – On-Line Resource with Energy Offer Curve; | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA)
3.9.1(5)(b)(i)(D) | ONDSR – On-Line Dynamically Scheduled Resource (DSR); | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA)
3.9.1(5)(b)(i)(E) | ONOS – On-Line Resource with Output Schedule; | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA)
3.9.1(5)(b)(i)(F) | ONOSREG – On-Line Resource with Output Schedule providing Regulation Service; | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA)
3.9.1(5)(b)(i)(G) | ONDSRREG – On-Line DSR providing Regulation Service; | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA)
3.9.1(5)(b)(i)(H) | FRRSUP – Available for Dispatch of Fast Responding Regulation Service (FRRS). This Resource Status is only to be used for Real-Time telemetry purposes; | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA)
3.9.1(5)(b)(i)(I) | ONTEST – On-Line blocked from SCED for operations testing (while ONTEST, a Generation Resource may be shown on Outage in the Outage Scheduler); | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA)
3.9.1(5)(b)(i)(J) | ONEMR – On-Line EMR (available for commitment or dispatch only for ERCOT-declared Emergency Conditions; the QSE may appropriately set LSL and High Sustained Limit (HSL) to reflect operating limits); | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA)
3.9.1(5)(b)(i)(K) | ONRR – On-Line as a synchronous condenser (hydro) providing Responsive Reserve (RRS) but unavailable for Dispatch by SCED and available for commitment by RUC; | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA)
3.9.1(5)(b)(i)(L) | ONECRS – On-Line as a synchronous condenser providing ERCOT Contingency Response Service (ECRS) but unavailable for Dispatch by SCED and available for commitment by RUC; | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA)
3.9.1(5)(b)(i)(M) | ONOPTOUT – On-Line and the hour is a RUC Buy-Back Hour; | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA)
3.9.1(5)(b)(i)(N) | SHUTDOWN – The Resource is On-Line and in a shutdown sequence, and has no Ancillary Service Obligations other than Off-Line Non-Spinning Reserve (Non-Spin) which the Resource will provide following the shutdown. This Resource Status is only to be used for Real-Time telemetry purposes; and | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA)
3.9.1(5)(b)(i)(O) | STARTUP – The Resource is On-Line and in a start-up sequence and has no Ancillary Service Obligations. This Resource Status is only to be used for Real-Time telemetry purposes. | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA)
3.9.1(5)(b)(i)(P) | OFFQS – Off-Line but available for SCED deployment. Only qualified Quick Start Generation Resources (QSGRs) may utilize this status. | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA)
3.9.1(5)(b)(i)(Q) | ONFFRRRS – Available for Dispatch of RRS when providing Fast Frequency Response (FFR) from Generation Resources. This Resource Status is only to be used for Real-Time telemetry purposes. A Resource with this Resource Status may also be providing Ancillary Services other than FFR; and |  |  | X | 2 seconds | Continuous | ICCP naming convention Private WAN point-to-point connection
3.9.1(5)(b)(i)(R) | ONHOLD – Resource is On-Line but temporarily unavailable for Dispatch by SCED or for participating in Ancillary Services. This Resource Status is only to be used for Real-Time telemetry purposes. For SCED, Resource Base Points will be set equal to the telemetered net real power of the Resource available at the time of the SCED execution. |  |  | X | 2 seconds | Continuous | ICCP naming convention Private WAN point-to-point connection
3.9.1(5)(b)(ii) | Select one of the following for Off-Line Generation Resources not synchronized to the ERCOT System that best describes the Resource’s status. These Resource Statuses are to be used for COP and/or Real-Time telemetry purposes, as appropriate. | Intro | Intro | Intro
3.9.1(5)(b)(ii)(A) | OUT – Off-Line and unavailable, or not connected to the ERCOT System and operating in a Private Microgrid Island (PMI); | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA)
3.9.1(5)(b)(ii)(B) | OFFNS – Off-Line but reserved for Non-Spin; | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA)
3.9.1(5)(b)(ii)(C) | OFF – Off-Line but available for commitment in the Day-Ahead Market (DAM) and RUC; and | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA)
3.9.1(5)(b)(ii)(D) | EMR – Available for commitment as a Resource contracted by ERCOT under Section 3.14.1, Reliability Must Run, or under paragraph (2) (4) of Section 6.5.1.1, ERCOT Control Area Authority, or available for commitment only for ERCOT-declared Emergency Condition events; the QSE may appropriately set LSL and HSL to reflect operating limits; and | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA)
3.9.1(5)(b)(ii)(E) | EMRSWGR - Switchable Generation Resource (SWGR) operating in a non-ERCOT Control Area, or in the case of a Combined Cycle Train with one or more SWGRs, a configuration in which one or more of the physical units in that configuration are operating in a non-ERCOT Control Area. | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA)
3.9.1(5)(b)(iii) | Select one of the following for Load Resources. Unless otherwise provided below, these Resource Statuses are to be used for COP and/or Real-Time telemetry purposes. | Intro | Intro | Intro
3.9.1(5)(b)(iii)(A) | ONRGL – Available for Dispatch of Regulation Service by Load Frequency Control (LFC) and, for any remaining Dispatchable capacity, by SCED with an Real-Time Market (RTM) Energy Bid; | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA)
3.9.1(5)(b)(iii)(B) | FRRSUP – Available for Dispatch of FRRS by LFC and not Dispatchable by SCED. This Resource Status is only to be used for Real-Time telemetry purposes; |  |  | X | 2 seconds | Continuous | ICCP naming convention Private WAN point-to-point connection
3.9.1(5)(b)(iii)(C) | FRRSDN - Available for Dispatch of FRRS by LFC and not Dispatchable by SCED. This Resource Status is only to be used for Real-Time telemetry purposes; |  |  | X | 2 seconds | Continuous | ICCP naming convention Private WAN point-to-point connection
3.9.1(5)(b)(iii)(D) | ONCLR – Available for Dispatch as a Controllable Load Resource by SCED with an RTM Energy Bid; | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA)
3.9.1(5)(b)(iii)(E) | ONRL – Available for Dispatch of RRS or Non-Spin, excluding Controllable Load Resources. A Load Resource, excluding Controllable Load Resources, may not provide ECRS with this Resource Status; | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA)
3.9.1(5)(b)(iii)(F) | ONECL – Available for Dispatch of ECRS or available for Dispatch of ECRS and RRS simultaneously, excluding Controllable Load Resources; | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA)
3.9.1(5)(b)(iii)(G) | OUTL – Not available; | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA)
3.9.1(5)(b)(iii)(H) | ONFFRRRSL – Available for Dispatch of RRS, excluding Controllable Load Resources. This Resource Status is only to be used for Real-Time telemetry purposes; | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA)
3.9.1(5)(c) | The HSL; | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA)
3.9.1(5)(c)(i) | For Load Resources other than Controllable Load Resources, the HSL should equal the expected power consumption; | Intro | Intro | Intro
3.9.1(5)(d) | The LSL; | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA)
3.9.1(5)(d)(i) | For Load Resources other than Controllable Load Resources, the LSL should equal the expected Low Power Consumption (LPC); | Intro | Intro | Intro
3.9.1(5)(e) | The High Emergency Limit (HEL); | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA)
3.9.1(5)(f) | The Low Emergency Limit (LEL); and | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA)
3.9.1(5)(g) | Ancillary Service Resource Responsibility capacity in MW for: | Intro | Intro | Intro
3.9.1(5)(g)(i) | Regulation Up Service (Reg-Up); | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA)
3.9.1(5)(g)(ii) | Regulation Down Service (Reg-Down); | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA)
3.9.1(5)(g)(iii) | RRS; | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA)
3.9.1(5)(g)(iv) | ECRS; and | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA)
3.9.1(5)(g)(v) | Non-Spin. | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA)
3.9.1(6) | For Combined Cycle Generation Resources, the above items are required for each operating configuration. In each hour only one Combined Cycle Generation Resource in a Combined Cycle Train may be assigned one of the On-Line Resource Status codes described above. | Intro | Intro | Intro
3.10.1 | Time Line for Network Operations Model Changes | Header | Header | Header
3.10.1(3) | TSPs and Resource Entities shall submit Network Operations Model updates at least three months prior to the physical equipment change. ERCOT shall update the Network Operations Model according to the following table (see table in protocols) | X |  |  | As needed | At least 3 months prior to the physical equipment changes | NOMCR Encrypted via https; authenticated via Digital Certificate
3.10.6 | QSE and Resource Entity Responsibilities | Header | Header | Header
3.10.6 (1) | Resource Entities shall provide Resource Registration data pursuant to Planning Guide Section 6.8.2, Resource Registration Process, to ERCOT and to TSPs upon request. The Resource Registration data will contain information describing each Generation Resource, SOG, and Load Resource that it represents under Section 3.10.7.2, Modeling of Resources and Transmission Loads. | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Resource Registration Encrypted via https; authenticated via Digital Certificate
3.10.6(3) | For each Generation Resource and Energy Storage Resource (ESR), Resource Entities shall provide ERCOT the following temperature data: review cold weather temperature limits listed below annually and, if necessary, update those limits no later than October 1 each year. For each Generation Resource and ESR, Resource Entities shall review hot weather temperature limits listed below annually and, if necessary, update those limits no later than April 1 each year. | X Intro | Intro | Intro | Annually | Cold weather information by October 1 Hot weather information by April 1 | RFIs until system updates are made to Resource Registration Encrypted via https; authenticated via Digital Certificate
3.10.6(3)(a) | Cold weather temperature limits: | Header | Header | Header
3.10.6(3)(a)(i) | Minimum historical ambient dry bulb temperature in degrees Fahrenheit at which the Resource has operated without a Forced Outage or Startup Loading Failure due to cold weather after at least one complete winter Peak Load Season following the Resource’s Initial Synchronization date based on the previous five calendar years of historical data; and | X |  |  | Annually As needed | Cold weather information by October 1 At least annually, and within 30 days of identifying any change. | RFIs until system updates are made to Resource Registration Encrypted via https; authenticated via Digital Certificate
3.10.6(3)(a)(ii) | Minimum historical ambient dry bulb temperature in degrees Fahrenheit at which the Resource has operated without experiencing a Forced Derate greater than 10 MW and 5% of its winter Seasonal net maximum rating due to cold weather after at least one complete winter Peak Load Season following the Resource’s Initial Synchronization date based on the previous five calendar years of historical data; and | X |  |  | Annually As needed | Cold weather information by October 1 At least annually, and within 30 days of identifying any change. | RFIs until system updates are made to Resource Registration Encrypted via https; authenticated via Digital Certificate
3.10.6(3)(a)(iii) | At least one of the following: | Header | Header | Header
3.10.6(3)(a)(iii)(A) | Minimum ambient dry bulb temperature in degrees Fahrenheit at which the Resource was designed to operate without a Forced Derate greater than 10 MW and 5% of its winter Seasonal net maximum sustainable rating; or | X |  |  | Annually As needed | Cold weather information by October 1 At least once every seven years, and within 30 days of identifying any change. | RFIs until system updates are made to Resource Registration Encrypted via https; authenticated via Digital Certificate
3.10.6(3)(a)(iii)(B) | Minimum ambient dry bulb temperature in degrees Fahrenheit at which the Resource can operate without a Forced Derate greater than 10 MW and 5% of its winter Seasonal net maximum sustainable rating determined by an engineering analysis; and | X |  |  | Annually As needed | Cold weather information by October 1 At least once every seven years, and within 30 days of identifying any change. | RFIs until system updates are made to Resource Registration Encrypted via https; authenticated via Digital Certificate
3.10.6(3)(a)(iv) | At least one of the following: | Header | Header | Header
3.10.6(3)(a)(iv)(A) | Minimum ambient dry bulb temperature in degrees Fahrenheit at which the Resource was designed to operate without a Forced Outage or Startup Loading Failure; or | X |  |  | Annually As needed | Cold weather information by October 1 At least once every seven years, and within 30 days of identifying any change. | RFIs until system updates are made to Resource Registration Encrypted via https; authenticated via Digital Certificate
3.10.6(3)(a)(iv)(B) | Minimum ambient dry bulb temperature in degrees Fahrenheit at which the Resource can operate without a Forced Outage or Startup Loading Failure determined by an engineering analysis. | X |  |  | Annually As needed | Cold weather information by October 1 At least once every seven years, and within 30 days of identifying any change. | RFIs until system updates are made to Resource Registration Encrypted via https; authenticated via Digital Certificate
3.10.6(3)(b) | Hot weather temperature limits: | Header | Header | Header
3.10.6(3)(b)(i) | Maximum historical ambient dry bulb temperature in degrees Fahrenheit at which the Resource has operated without experiencing a Forced Outage or Startup Loading Failure due to hot weather after at least one complete summer Peak Load Season following the Resource’s Initial Synchronization date based on the previous five years of historical data; and | X |  |  | Annually As needed | Hot weather information by April 1 At least annually and within 30days of identifying any change. | RFIs until system updates are made to Resource Registration Encrypted via https; authenticated via Digital Certificate
3.10.6(3)(b)(ii) | Maximum historical ambient dry bulb temperature in degrees Fahrenheit at which the Resource has operated without experiencing a Forced Derate greater than 10 MW and 5% of its summer Seasonal net maximum sustainable rating due to hot weather after at least one complete summer Peak Load Season following the Resource’s Initial Synchronization date based on the previous five calendar years of historical data; and | X |  |  | Annually As needed | Hot weather information by April 1 At least annually and within 30days of identifying any change. | RFIs until system updates are made to Resource Registration Encrypted via https; authenticated via Digital Certificate
3.10.6(3)(b)(iii) | At least one of the following: | Header | Header | Header
3.10.6(3)(b)(iii)(A) | Maximum ambient dry bulb temperature in degrees Fahrenheit at which the Resource was designed to operate without a Forced Derate greater than 10 MW and 5% of its summer Seasonal net maximum sustainable rating; or | X |  |  | Annually As needed | Hot weather information by April 1 At least once every seven years, and within 30 days of identifying any change. | RFIs until system updates are made to Resource Registration Encrypted via https; authenticated via Digital Certificate
3.10.6(3)(b)(iii)(B) | Maximum ambient dry bulb temperature in degrees Fahrenheit at which the Resource was designed to operate without a Forced Derate greater than 10 MW and 5% of its summer Seasonal net maximum sustainable rating; or | X |  |  | Annually As needed | Hot weather information by April 1 At least once every seven years, and within 30 days of identifying any change. | RFIs until system updates are made to Resource Registration Encrypted via https; authenticated via Digital Certificate
3.10.6(3)(b)(iv) | At least one of the following: | Header | Header | Header
3.10.6(3)(b)(iv)(A) | Maximum ambient dry bulb temperature in degrees Fahrenheit at which the Resource was designed to operate without a Forced Outage or Startup Loading Failure; or | X |  |  | Annually As needed | Hot weather information by April 1 At least once every seven years, and within 30 days of identifying any change. | RFIs until system updates are made to Resource Registration Encrypted via https; authenticated via Digital Certificate
3.10.6(3)(b)(iv)(B) | Maximum ambient dry bulb temperature in degrees Fahrenheit at which the Resource can operate without a Forced Outage or Startup Loading Failure, determined by an engineering analysis. | X |  |  | Annually As needed | Hot weather information by April 1 At least once every seven years, and within 30 days of identifying any change. | RFIs until system updates are made to Resource Registration Encrypted via https; authenticated via Digital Certificate
3.10.6(4) | Each Resource Entity shall review at least annually the temperatures once every seven years for each Generation Resource and ESR the minimum and maximum ambient dry bulb temperature at which the Resource can operate, as described in paragraphs (3)(a)(i), (3)(a)(ii), (3)(b)(i), and (3)(b)(ii) (3)(a)(iii), (3)(a)(iv), (3)(b)(iii), and (3)(b)(iv) above and shall update each Resource’s Registration data accordingly if necessary within 30 days of identifying any change in these temperatures. | X |  |  | Every 7 years At least annually | At least annually and within 30days of identifying any change. | RFIs until system updates are made to Resource Registration Encrypted via https; authenticated via Digital Certificate
3.10.6(5) | Each Resource Entity shall review at least once every seven years the temperatures described in paragraphs (3)(a)(iii), (3)(a)(iv), (3)(b)(iii), and (3)(b)(iv) above and shall update each Resource’s Registration data within 30 days of identifying any change in these temperatures. | X |  |  | Every 7 years | At least once every seven years, and within 30 days of identifying any change. | RFIs until system updates are made to Resource Registration Encrypted via https; authenticated via Digital Certificate
3.10.6(5)(6) | Resource Entities shall update each Generation Resource’s alternate fuel information within 30 calendar days of any changes to the alternate fuel information. | X |  |  | Within 30 calendar days of any changes As needed | Within 30 calendar days of any changes | RFIs until system updates are made to Resource Registration Encrypted via https; authenticated via Digital Certificate
3.10.7.1.1 | Transmission Lines | Header | Header | Header
3.10.7.1.1(2) | For each of its transmission lines operated as part of the ERCOT Transmission Grid, each TSP and if applicable, Resource Entity, shall provide ERCOT with the following information consistent with the ratings methodology prescribed in the ERCOT Operating Guides: | Intro | Intro | Intro
3.10.7.1.1(2)(a) | Equipment owner(s); | X |  |  | As needed | At least 3 months prior to the physical equipment changes | NOMCR Encrypted via https; authenticated via Digital Certificate
3.10.7.1.1(2)(b) | Equipment operator(s); | X |  |  | As needed | At least 3 months prior to the physical equipment changes | NOMCR Encrypted via https; authenticated via Digital Certificate
3.10.7.1.1(2)(c) | Transmission Element name; | X |  |  | As needed | At least 3 months prior to the physical equipment changes | NOMCR Encrypted via https; authenticated via Digital Certificate
3.10.7.1.1(2)(d) | Line impedance; | X |  |  | As needed | At least 3 months prior to the physical equipment changes | NOMCR Encrypted via https; authenticated via Digital Certificate
3.10.7.1.1(2)(e) | Normal Rating, Emergency Rating, 15-Minute Rating, Conductor/Transformer 2-Hour Rating, and Relay Loadability Rating; and | X |  |  | As needed | At least 3 months prior to the physical equipment changes | NOMCR Encrypted via https; authenticated via Digital Certificate
3.10.7.1.1(2)(f) | Other data necessary to model Transmission Element(s). | X |  |  | As needed | At least 3 months prior to the physical equipment changes | NOMCR Encrypted via https; authenticated via Digital Certificate
3.10.7.1.1(4) | The TSP and Resource Entity may implement protective relay and control systems and set values appropriate to de-energize faulted equipment and meet the TSP and Resource Entity obligations for public or employee safety, and when necessary to prevent in-service or premature equipment failure consistent with Good Utility Practice and accepted industry standards. The TSP and Resource Entity shall include those limits as Relay Loadability Ratings when providing ERCOT with ratings or proposed transfer limits. | X |  |  | As needed | At least 3 months prior to the physical equipment changes | NOMCR Encrypted via https; authenticated via Digital Certificate
3.10.7.1.2 | Transmission Buses | Header | Header | Header
3.10.7.1.2(2) | Each TSP and if applicable, Resource Entity, shall provide ERCOT with the following information, subject to the naming conventions in Section 3.10.7.1, Modeling of Transmission Elements and Parameters: | Intro | Intro | Intro
3.10.7.1.2(2)(a) | Equipment owner(s); | X |  |  | As needed | At least 3 months prior to the physical equipment changes | NOMCR Encrypted via https; authenticated via Digital Certificate
3.10.7.1.2(2)(b) | Equipment operator(s); | X |  |  | As needed | At least 3 months prior to the physical equipment changes | NOMCR Encrypted via https; authenticated via Digital Certificate
3.10.7.1.2(2)(c) | The Transmission Element name; | X |  |  | As needed | At least 3 months prior to the physical equipment changes | NOMCR Encrypted via https; authenticated via Digital Certificate
3.10.7.1.2(2)(d) | The substation name; | X |  |  | As needed | At least 3 months prior to the physical equipment changes | NOMCR Encrypted via https; authenticated via Digital Certificate
3.10.7.1.2(2)(e) | A description of all transmission circuits that may be connected through breakers or switches; and | X |  |  | As needed | At least 3 months prior to the physical equipment changes | NOMCR Encrypted via https; authenticated via Digital Certificate
3.10.7.1.2(2)(f) | Other data necessary to model Transmission Element(s). | X |  |  | As needed | At least 3 months prior to the physical equipment changes | NOMCR Encrypted via https; authenticated via Digital Certificate
3.10.7.1.3 | Transmission Breakers and Switches | Header | Header | Header
3.10.7.1.3(2) | Each TSP and Resource Entity shall provide ERCOT with the following information, subject to the naming conventions in Section 3.10.7.1, Modeling of Transmission Elements and Parameters: | Into | Intro | Intro
3.10.7.1.3(2)(a) | Equipment owner(s); | X |  |  | As needed | At least 3 months prior to the physical equipment changes | NOMCR Encrypted via https; authenticated via Digital Certificate
3.10.7.1.3(2)(b) | Equipment operator(s); | X |  |  | As needed | At least 3 months prior to the physical equipment changes | NOMCR Encrypted via https; authenticated via Digital Certificate
3.10.7.1.3(2)(c) | The Transmission Element name; | X |  |  | As needed | At least 3 months prior to the physical equipment changes | NOMCR Encrypted via https; authenticated via Digital Certificate
3.10.7.1.3(2)(d) | The substation name; | X |  |  | As needed | At least 3 months prior to the physical equipment changes | NOMCR Encrypted via https; authenticated via Digital Certificate
3.10.7.1.3(2)(e) | Connectivity; | X |  |  | As needed | At least 3 months prior to the physical equipment changes | NOMCR Encrypted via https; authenticated via Digital Certificate
3.10.7.1.3(2)(f) | Normal status; | X |  |  | As needed | At least 3 months prior to the physical equipment changes | NOMCR Encrypted via https; authenticated via Digital Certificate
3.10.7.1.3(2)(g) | Synchronism check relay phase angle limits that are applied to operator-initiated, non-automated control actions of TSP-owned transmission breakers; and | X |  |  | As needed | At least 3 months prior to the physical equipment changes | NOMCR Encrypted via https; authenticated via Digital Certificate
3.10.7.1.3(2)(h) | Other data necessary to model Transmission Element(s). | X |  |  | As needed | At least 3 months prior to the physical equipment changes | NOMCR Digital Certificate/Citrix
3.10.7.1.3(3) | ERCOT shall develop methods to accurately model changes in transmission line loading resulting from Load rollover schemes transferring more than ten MW. This may include modeling distribution circuit breakers, dead line sensing, or other methods that signal when the Load should be transferred from one transmission line to another transmission line. ERCOT may employ heuristic rule sets for all manual Load transfers and for automated transfers where feasible. ERCOT application software is required to model the effects of automatic or manual schemes in the field transfer Load under line outage conditions. Each TSP and as applicable, Resource Entity, shall define the Load rollover schemes under Section 3.10.7.2, Modeling of Resources and Transmission Loads, and furnish this information to ERCOT. Transmission field (right-of-way) switches must be connected to a named Electrical Bus and be included in the Network Operations Model. | X |  |  | As needed | At least 3 months prior to the physical equipment changes | NOMCR Encrypted via https; authenticated via Digital Certificate
3.10.7.1.4 | Transmission, Main Power Transformers (MPTs) and Generation Resource Step-Up Transformers | Header | Header | Header
3.10.7.1.4(3) | Each TSP and Resource Entity shall provide ERCOT with information to accurately describe each transformer in the Network Operations Model including any tertiary Load as required by ERCOT. Each TSP and Resource Entity shall provide ERCOT with the following information, subject to the naming conventions in Section 3.10.7.1, Modeling of Transmission Elements and Parameters: | Intro | Intro | Intro
3.10.7.1.4(3)(a) | Equipment owner(s); | X |  |  | As needed | At least 3 months prior to the physical equipment changes | NOMCR Encrypted via https; authenticated via Digital Certificate
3.10.7.1.4(3)(b) | Equipment operator(s); | X |  |  | As needed | At least 3 months prior to the physical equipment changes | NOMCR Encrypted via https; authenticated via Digital Certificate
3.10.7.1.4(3)(c) | The Transmission Element name; | X |  |  | As needed | At least 3 months prior to the physical equipment changes | NOMCR Encrypted via https; authenticated via Digital Certificate
3.10.7.1.4(3)(d) | The substation name; | X |  |  | As needed | At least 3 months prior to the physical equipment changes | NOMCR Encrypted via https; authenticated via Digital Certificate
3.10.7.1.4(3)(e) | Winding ratings, including Normal Rating, Emergency Rating, 15-Minute Rating, Conductor/Transformer 2-Hour Rating, and Relay Loadability Rating; | X |  |  | As needed | At least 3 months prior to the physical equipment changes | NOMCR Encrypted via https; authenticated via Digital Certificate
3.10.7.1.4(3)(f) | Connectivity; | X |  |  | As needed | At least 3 months prior to the physical equipment changes | NOMCR Encrypted via https; authenticated via Digital Certificate
3.10.7.1.4(3)(g) | Transformer parameters, including all tap parameters; and | X |  |  | As needed | At least 3 months prior to the physical equipment changes | NOMCR Encrypted via https; authenticated via Digital Certificate
3.10.7.1.4(3)(h) | Other data necessary to model Transmission Element(s). | X |  |  | As needed | At least 3 months prior to the physical equipment changes | NOMCR Encrypted via https; authenticated via Digital Certificate
3.10.7.1.5 | Reactors, Capacitors, and other Reactive Controlled Sources | Header | Header | Header
3.10.7.1.5(2) | Each Market Participant shall provide ERCOT with the following information, subject to the naming conventions in Section 3.10.7.1, Modeling of Transmission Elements and Parameters: | Intro | Intro | Intro
3.10.7.1.5(2)(a) | Equipment owner(s); | X |  |  | As needed | At least 3 months prior to the physical equipment changes | NOMCR Encrypted via https; authenticated via Digital Certificate
3.10.7.1.5(2)(b) | Equipment operator(s); | X |  |  | As needed | At least 3 months prior to the physical equipment changes | NOMCR Encrypted via https; authenticated via Digital Certificate
3.10.7.1.5(2)(c) | The Transmission Element name; | X |  |  | As needed | At least 3 months prior to the physical equipment changes | NOMCR Encrypted via https; authenticated via Digital Certificate
3.10.7.1.5(2)(d) | The substation name; | X |  |  | As needed | At least 3 months prior to the physical equipment changes | NOMCR Encrypted via https; authenticated via Digital Certificate
3.10.7.1.5(2)(e) | Voltage or time switched on; | X |  |  | As needed | At least 3 months prior to the physical equipment changes | NOMCR Encrypted via https; authenticated via Digital Certificate
3.10.7.1.5(2)(f) | Voltage or time switched off; | X |  |  | As needed | At least 3 months prior to the physical equipment changes | NOMCR Encrypted via https; authenticated via Digital Certificate
3.10.7.1.5(2)(g) | Associated switching device name; | X |  |  | As needed | At least 3 months prior to the physical equipment changes | NOMCR Encrypted via https; authenticated via Digital Certificate
3.10.7.1.5(2)(h) | Connectivity; | X |  |  | As needed | At least 3 months prior to the physical equipment changes | NOMCR Encrypted via https; authenticated via Digital Certificate
3.10.7.1.5(2)(i) | Nominal voltage and associated capacitance or reactance; and | X |  |  | As needed | At least 3 months prior to the physical equipment changes | NOMCR Encrypted via https; authenticated via Digital Certificate
3.10.7.1.5(2)(j) | Other data necessary to model Transmission Element(s). | X |  |  | As needed | At least 3 months prior to the physical equipment changes | NOMCR Encrypted via https; authenticated via Digital Certificate
3.10.7.2 | Modeling of Resources and Transmission Loads | Header | Header | Header
3.10.7.2(1) | Each Resource Entity shall provide ERCOT and its interconnecting TSP with information describing each of its Generation Resources, SOGs, and Load Resources connected to the ERCOT System. All Transmission Generation Resources (TGRs), Settlement Only Transmission Generators (SOTGs), Settlement Only Transmission Self-Generators (SOTSGs), and the non-TSP owned MPTs greater than ten MVA, must be modeled to provide equivalent generation injections to the ERCOT Transmission Grid. ERCOT shall coordinate the modeling of Generation Resources, Private Use Networks, and Load Resources with their owners to ensure consistency between TSP models and ERCOT models. | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Resource Registration Encrypted via https; authenticated via Digital Certificate
3.10.7.2(6) | ERCOT shall create a DC Tie Resource to represent an equivalent generation injection to represent the flow into the ERCOT Transmission Grid from operation of DC Ties. The actual injection flow on the DC Tie from telemetry provided by the facility owner(s) is the DC Tie Resource output. | X | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection (RTA)
3.10.7.3 | Modeling of Private Use Networks | Header | Header | Header
3.10.7.3 (1) | ERCOT shall create and use network models describing Private Use Networks according to the following: | Intro | Intro | Intro
3.10.7.3(1)(a) | A Generation Entity with a Resource located within a Private Use Network shall provide data to ERCOT, for use in the Network Operations Model, for each of its individual generating unit(s) located within the Private Use Network in accordance with Section 3.3.2.1, Information to Be Provided to ERCOT, if it meets any one of the following criteria: | X |  |  | As needed | At least 3 months prior to the physical equipment changes | NOMCR Encrypted via https; authenticated via Digital Certificate
3.10.7.3(1)(a)(i) | Contains a generator greater than ten MW and is registered with the PUCT according to P.U.C. Subst. R. 25.109, Registration of Power Generation Companies and Self-Generators, as a power generation company; or | X |  |  | As needed | At least 3 months prior to the physical equipment changes | NOMCR Encrypted via https; authenticated via Digital Certificate
3.10.7.3(1)(a)(ii) | Is part of a Private Use Network which contains more than one connection to the ERCOT Transmission Grid; or | X |  |  | As needed | At least 3 months prior to the physical equipment changes | NOMCR Encrypted via https; authenticated via Digital Certificate
3.10.7.3(1)(a)(iii) | Contains generation registered to provide Ancillary Services. | X |  |  | As needed | At least 3 months prior to the physical equipment changes | NOMCR Encrypted via https; authenticated via Digital Certificate
3.10.7.3(1)(b) | A Generation Entity with an SOTSG shall provide to ERCOT annually, or more often upon change, the following information for ERCOT's use in the Network Operations Mondel, for each of its individual generating unit(s) located within the Private Use Network: | Intro | Intro | Intro
3.10.7.3(1)(b)(i) | Equipment owner(s); | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Resource Registration Encrypted via https; authenticated via Digital Certificate
3.10.7.3(1)(b)(ii) | Equipment operator(s); | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Resource Registration Encrypted via https; authenticated via Digital Certificate
3.10.7.3(1)(b)(iii) | TSP substation name connecting the Private Use Network to the ERCOT System; | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Resource Registration Encrypted via https; authenticated via Digital Certificate
3.10.7.3(1)(b)(iv) | At the request of ERCOT, a description of Transmission Elements within the Private Use Network that may be connected through breakers or switches; | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Resource Registration Encrypted via https; authenticated via Digital Certificate
3.10.7.3(1)(b)(v) | Net energy delivery metering, as required by ERCOT, to and from a the Private Use Network and the ERCOT System at the POIB; | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Resource Registration Encrypted via https; authenticated via Digital Certificate
3.10.7.3(1)(b)(vi) | For each individual generator located within the Private Use Network, the gross capacity in MW and its reactive capability curve; | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Resource Registration Encrypted via https; authenticated via Digital Certificate
3.10.7.3(1)(b)(vii) | Maximum and minimum reasonability limits of the Load located within the Private Use Network; | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Resource Registration Encrypted via https; authenticated via Digital Certificate
3.10.7.3(1)(b)(viii) | Outage schedule for each generation unit located within the Private Use Network, updated as changes occur from the annually submitted information; and | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Resource Registration Encrypted via https; authenticated via Digital Certificate
3.10.7.3(1)(b)(ix) | Other interconnection data as required by ERCOT. | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Resource Registration Encrypted via https; authenticated via Digital Certificate
3.10.7.3(1)(e) | ERCOT may require the owner or operator of a Private Use Network to provide information to ERCOT and the TSP on Transmission Facilities located within the Private Use Network for use in the Network Operations Model if the information is required to adequately model and determine the security of the ERCOT Transmission Grid, including data to perform loop flow analysis of Private Use Networks. | X |  |  | As needed | At least 3 months prior to the physical equipment changes | Resource Registration Encrypted via https; authenticated via Digital Certificate
3.10.7.5.1 | Continuous Telemetry of the Status of Breakers and Switches | Header | Header | Header
3.10.7.5.1(1) | Each TSP and QSE shall be responsible for provideing telemetry, as described in this subsection, to ERCOT on the status of all breakers and switches it owns or its Resource owns, respectively, used to switch any Transmission Element or Load modeled by ERCOT. | X | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection (RTA)
3.10.7.5.1(3) | Each TSP, Resource Entity, or QSE shall update the status of any breaker or switch it owns or is responsible for through manual entries, if necessary, to communicate the actual current state of the device to ERCOT, except if the change in state is expected to return to the prior state within one minute. | X | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection (RTA)
3.10.7.5.2 | Continuous Telemetry of the Real-Time Measurements of Bus Load, Voltages, Tap Position, and Flows | Header | Header | Header
3.10.7.5.2(1) | Each TSP and QSE shall provide telemetry of voltages, flows, and Loads on any modeled Transmission Element it owns or its Resource Entity owns, respectively, to the extent such may be required to estimate all transmission Load withdrawals and generation injections to and from the ERCOT Transmission Grid using the State Estimator and as needed to meet the State Estimator requirements set forth in Section 3.10.9, State Estimator Requirements, with consideration given to the economic implications of inaccurate LMP results versus the cost to remedy. | X | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection (RTA)
3.10.7.5.2(8) | Each TSP shall designate which telemetered measurement of the POIB voltage shall be utilized to determine compliance with Voltage Set Point instructions, and then update the designation as necessary in the Network Operations Model by submitting a NOMCR. Each TSP shall telemeter this POI kV bus measurement to ERCOT. If the TSP cannot provide a kV bus measurement at the POI, the TSP may propose an alternate location subject to ERCOT approval. |  |  | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
3.10.7.5.3 | Required Telemetry of Voltage and Power Flow | Header | Header | Header
3.10.7.5.3(1) | QSEs, Resource Entities and TSPs as indicated in each subsection below shall provide power operation data to ERCOT, including, but not limited to: | Intro | Intro | Intro
3.10.7.5.3(1)(a) | Real-Time generation data from QSEs; |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
3.10.7.5.3(1)(b) | Planned and Forced Outage information from QSEs; | X |  |  | As soon as reasonably practicable | If Forced outages remains longer than two hours | Outage Scheduler Encrypted via https; authenticated via Digital Certificate
3.10.7.5.3(1)(c) | Network data from TSPs and QSEs , including: | Intro | Intro | Intro
3.10.7.5.3(1)(c)(i) | Breaker and line switch status of all ERCOT Transmission Grid devices; | X | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection (RTA)
3.10.7.5.3(1)(c)(ii) | Line flow MW and MVAr; | X | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection (RTA)
3.10.7.5.3(1)(c)(iii) | Breaker and switch status connected to any Resource; | X | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection (RTA)
3.10.7.5.3(1)(c)(iv) | Transmission Facility voltages; and | X | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection (RTA)
3.10.7.5.3(1)(c)(v) | Transformer MW, MVAr and tap; | X | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection (RTA)
3.10.7.5.3(1)(d) | Real-Time generation and Load Resource meter data from QSEs; | X | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection (RTA)
3.10.7.5.3(1)(e) | Real-Time generation meter splitting signal from QSEs; | X | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection (RTA)
3.10.7.5.3(1)(f) | Transmission Facility Planned and Forced Outage information from TSPs; | X |  |  | Continually and As it occurs | Planned: per section 3.1.5.3 of the Protocols Forced: If outages remains longer than two hours | Outage Scheduler Encrypted via https; authenticated via Digital Certificate
3.10.7.5.3(1)(g) | Network transmission data (model and constraints) from TSPs; and | X |  |  | As needed | At least 3 months prior to the physical equipment changes | NOMCR Encrypted via https; authenticated via Digital Certificate
3.10.7.5.3(1)(h) | Resource modeling data, including any Resource owned transmission equipment data from Resource entity; and | X |  |  | As needed | At least 3 months prior to the physical equipment changes | NOMCR Encrypted via https; authenticated via Digital Certificate
3.10.8.1 | Dynamic Ratings Delivered via ICCP | Header | Header | Header
3.10.8.1(1) | The TSP shall supply the following, via ICCP, updated at least every ten minutes: | Intro | Intro | Intro
3.10.8.1(1)(a) | Normal Rating; and |  | X | X | At least every ten minutes | Ten minutes | ICCP Naming Convention Private WAN point-to-point connection
3.10.8.1(1)(b) | Optionally Emergency Rating and/or 15-Minute Rating (required when Emergency Rating is provided). |  | X | X | At least every ten minutes | Ten minutes | ICCP Naming Convention Private WAN point-to-point connection
3.10.8.5 | Transmission Service Provider Responsibilities Related to Dynamic Ratings | Header | Header | Header
3.10.8.5(1) | Each TSP shall: | Intro | Intro | Intro
3.10.8.5(1)(a) | Provide ERCOT with tables of ratings for different ambient temperatures for Transmission Elements, as requested by ERCOT. | X |  |  | As needed | Within 2 months | NOMCR Encrypted via https; authenticated via Digital Certificate
3.10.8.5(1)(b) | Submit within two months a temperature adjusted rating table when a request is received from ERCOT unless multiple requests are made by ERCOT within the two-month period or unusual circumstances prevent the request from being accommodated in a timely fashion. Such circumstances must be explained to ERCOT in writing and must be posted by ERCOT on the MIS Secure Area within five Business Days of receipt. | X |  |  | As needed | Within 2 months | NOMCR Encrypted via https; authenticated via Digital Certificate
3.10.8.5(1)(c) | Provide Real-Time temperatures for each Weather Zone in which the TSP has existing dynamically rated transmission equipment, or alternatively provide rating updates for each temperature-adjusted line rating updated at least once every ten minutes. |  | X | X | At least every ten minutes | Within 2 months | ICCP Naming Convention Private WAN point-to-point connection
3.13 | Renewable Production Potential Forecasts | Header | Header | Header
3.13(1) | ERCOT shall produce forecasts of Renewable Production Potential (RPP) for Wind-powered Generation Resources (WGRs) and PhotoVoltaic Generation Resources (PVGRs) to be used as an input into the Day-Ahead Reliability Unit Commitment (DRUC) and Hour-Ahead Reliability Unit Commitment (HRUC). ERCOT shall produce the forecasts using information provided by WGR/PVGR Entities, meteorological information, and Supervisory Control and Data Acquisition (SCADA). WGR and PVGR Entities shall install telemetry at their respective Resources and transmit the ERCOT-specified site-specific meteorological information to ERCOT. WGR and PVGR Entities shall also provide detailed equipment status at the WGR/PVGR facility as specified by ERCOT to support the RPP forecast. ERCOT shall post forecasts for each WGR and PVGR to the Qualified Scheduling Entities (QSEs) representing WGRs and/or PVGRs on the Market Information System (MIS) Certified Area. QSEs shall use the ERCOT-provided forecasts for WGRs/PVGRs throughout the Day-Ahead and Operating Day for applicable markets and Reliability Unit Commitments (RUCs). Similar requirements for run-of-the-river hydro must be developed as needed. | X |  | X | As soon as reasonably practicable and 2 seconds | No later than 60 minutes after the event and Continuous | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate / ICCP naming convention Private WAN point-to-point connection
3.15 | Voltage Support | Header | Header | Header
3.15(15) | All WGRs must provide a Real-Time SCADA point that communicates to ERCOT the number of wind turbines that are available for real power and/or Reactive Power injection into the ERCOT Transmission Grid. WGRs must also provide two other Real-Time SCADA points that communicate to ERCOT the following: |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
3.15(15)(a) | The number of wind turbines that are not able to communicate and whose status is unknown; and |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
3.15(15)(b) | The number of wind turbines out of service and not available for operation. |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
3.15(16) | All PhotoVoltaic Generation Resources (PVGRs) must provide a Real-Time SCADA point that communicates to ERCOT the capacity of PhotoVoltaic (PV) equipment that is available for real power and/or Reactive Power injection into the ERCOT Transmission Grid. PVGRs must also provide two other Real-Time SCADA points that communicate to ERCOT the following: |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
3.15(16)(a) | The capacity of PV equipment that is not able to communicate and whose status is unknown; and |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
3.15(16)(b) | The capacity of PV equipment that is out of service and not available for operation. |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
3.15.3(4) | Each Generation Resource providing VSS shall operate with the unit’s Automatic Voltage Regulator (AVR) in the automatic voltage control mode unless specifically directed to operate in manual mode by ERCOT, or when the unit is telemetering its Resource Status as STARTUP, SHUTDOWN, or ONTEST, or the QSE determines a need to operate in manual mode due to an undue threat to safety, undue risk of bodily harm, or undue damage to equipment at the generating plant. |  | X | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
3.15.3(9) | The Resource Entity for an IRR synchronized to the ERCOT System that is not capable of providing Reactive Power when not producing real power shall: | Intro | Intro | Intro
3.15.3(9)(d) | Send to ERCOT, via telemetry, an AVR status of “Off” when the IRR is synchronized to the ERCOT System and not producing Reactive Power. |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
4.4.4 | DC Tie Schedules | Header | Header | Header
4.4.4(8) | A QSE exporting from ERCOT and/or importing to ERCOT through a DC Tie shall: | Intro | Intro | Intro
4.4.4(8)(b) | Submit e-Tags for all proposed transactions; and | X |  |  | As needed | 15 minutes before the schedule ramps | OATI Encrypted via https; authenticated Digital Certificate
6.4.2.5 | DSR Load | Header | Header | Header
6.4.2.5(3)(a) | All power signals for DSR Load must be sent to ERCOT in Real-Time by telemetry; |  | X | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.4.6 | Resource Status | Header | Header | Header
6.4.6(1) | ERCOT shall use the telemetered Resource Status for all applications requiring status of Resources during the Operating Hour, including SCED and Load Frequency Control (LFC). QSEs shall provide ERCOT with accurate telemetry of the current capability of each Resource including the Resource Status, Ramp Rates, HSL, and LSL. |  | X | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.4.6(2)(a) | Each QSE shall provide the Real-Time operating status of each Resource to ERCOT by telemetry using the status codes in the COP for Real-Time as described in Section 3.9, Current Operating Plan (COP); |  | X | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.4.8 | Notification of Forced Outage of a Resource | Header | Header | Header
6.4.8(1) | In the event of a Forced Outage of a Resource, the telemetered status of the Resource automatically notifies ERCOT of the event. In the event of a Forced Outage, the telemetered Resource Status shall be changed to the appropriate Off-Line status as soon as practicable but no longer than 15 minutes after the Forced Outage occurs. |  | X | X | As needed | As soon as reasonably practicable but no longer than 15 minutes after the Forced Outage occurs | ICCP Naming Convention Private WAN point-to-point connection
6.4.8(2) | In the event of a Forced Outage or an impending Forced Outage, the Resource Entity or its designee shall inform ERCOT of the following in the Outage Scheduler: | X |  |  | As needed | As soon as reasonably practicable but no longer than 60 minutes after the Forced Outage occurs | Outage Scheduler Encrypted via https; authenticated Digital Certificate
6.4.8(2)(a) | Time of expected change in Resource Status or rating; | X |  |  | As needed | As soon as reasonably practicable but no longer than 60 minutes after the Forced Outage occurs | Outage Scheduler Encrypted via https; authenticated Digital Certificate
6.4.8(2)(b) | Text message describing the nature of the Forced Outage or de-rating updated as new information becomes available; and | X |  |  | As needed | As soon as reasonably practicable but no longer than 60 minutes after the Forced Outage occurs | Outage Scheduler Encrypted via https; authenticated Digital Certificate
6.4.8(2)(c) | The expected minimum and maximum duration of the Forced Outage or de-rating. | X |  |  | As needed | As soon as reasonably practicable but no longer than 60 minutes after the Forced Outage occurs | Outage Scheduler Encrypted via https; authenticated Digital Certificate
6.4.8(3) | In the event of a Forced Outage, the QSE must update the Resource’s COP as soon as practicable but no longer than 60 minutes after the Forced Outage occurs. | X |  |  | As needed | No later than 60 minutes after the event | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA)
6.4.8(4) | Each QSE shall timely update the telemetered Resource Status and COP unless in the reasonable judgment of the QSE, such compliance would create an undue threat to safety, undue risk of bodily harm, or undue damage to equipment. The QSE is excused from updating the telemetered Resource Status and/or COP only for so long as the undue threat to safety, undue risk of bodily harm, or undue damage to equipment exists. The time for updating the telemetered Resource Status and/or COP begins once the undue threat to safety, undue risk of bodily harm, or undue damage to equipment no longer exists. | X | X | X | As soon as reasonably practicable and as needed | No later than 60 minutes after the event and as needed | EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA) / ICCP naming convention Private WAN point-to-point connection (RTA)
6.5.5.1 | Changes in Resource Status | Header | Header | Header
6.5.5.1(1) | Each QSE shall notify ERCOT via telemetry of a change in Resource Status via telemetry that is not related to a Forced Outage as soon as practicable but no longer than 15 minutes after the change in status occurs and through changes in the Current Operating Plan (COP) as soon as practicable following but no longer than 60 minutes after the change in status of the Resource occurs. | X | X | X | As needed / 2 seconds | As needed / Continuous As soon as practicable but no longer than 15 minutes after the change in status occurs / As soon as practicable but no longer than 60 minutes after the change in status of the Resource occurs. | ICCP Naming Convention Private WAN point-to-point connection (RTA)/ EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA)
6.5.5.1(2) | When an On-Line Resource is experiencing an event that may affect its availability and/or capability and that requires further actions to stabilize the Resource and/or determine the impact of the event, the QSE may change the Resource Status to ONHOLD within 15 minutes of experiencing an event. Following this Resource Status change, the telemetered HSL and any other applicable telemetry of the Resource as specified in paragraph (2) of Section 6.5.5.2, Operational Data Requirements, shall be updated as soon as practicable but no longer than 15 minutes after the change in Resource Status to ONHOLD. After the QSE has determined the impact of the event, the QSE shall change the Resource Status to its updated status as soon as practicable but no longer than 60 consecutive minutes of being in the ONHOLD status. |  | X | X | As needed / 2 seconds | As soon as practicable but no longer than 15 minutes after the change in Resource Status to ONHOLD. | ICCP Naming Convention Private WAN point-to-point connection
6.5.5.1(3) | Each QSE shall promptly inform ERCOT when the operating mode of its Generation Resource’s Automatic Voltage Regulator (AVR) or Power System Stabilizer (PSS) is changed while the Resource is On-Line. The QSE shall also provide the Resource’s AVR or PSS status logs to ERCOT upon request. For each Generation Resource that is On-Line but not producing real power and is not capable of providing Reactive Power, each QSE must still telemeter its AVR status to ERCOT but is not required to provide verbal notifications of its AVR status changes to ERCOT during these operating conditions. |  | X | X | As needed | As soon as practicable | ICCP Naming Convention Private WAN point-to-point connection
6.5.5.1(5) | Each QSE shall timely update the telemetered Resource Status unless in the reasonable judgment of the QSE, such compliance would create an undue threat to safety, undue risk of bodily harm, or undue damage to equipment. The QSE is excused from updating the telemetered Resource Status only for so long as the undue threat to safety, undue risk of bodily harm, or undue damage to equipment exists. The time for updating the telemetered Resource Status begins once the undue threat to safety, undue risk of bodily harm, or undue damage to equipment no longer exists. |  | X | X | As needed / 2 seconds | As needed / Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.5.2 | Operational Data Requirements | Header | Header | Header
6.5.5.2(2) | A QSE representing a Generation Resource connected to Transmission Facilities or distribution facilities shall provide the following Real-Time telemetry data to ERCOT for each Generation Resource. | Intro | Intro | Intro
6.5.5.2(2)(a) | Net real power (in MW) as measured by installed power metering or as calculated in accordance with the Operating Guides based on metered gross real power and conversion constants determined by the Resource Entity and provided to ERCOT through the Resource Registration process. Net real power represents the actual generation of a Resource for all real power dispatch purposes, including use in Security-Constrained Economic Dispatch (SCED), determination of the High Ancillary Service Limit (HASL), High Dispatch Limit (HDL), Low Dispatch Limit (LDL) and Low Ancillary Service Limit (LASL), and is consistent with telemetered HSL, LSL and Non-Frequency Responsive Capacity (NFRC); | X | X | X | As needed / 2 seconds | As needed / Continuous | ICCP Naming Convention Private WAN point-to-point connection (RTA)/ EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA)
6.5.5.2(2)(b) | Gross real power (in MW) as measured by installed power metering or as calculated in accordance with the Operating Guides based on metered real power, which may include Supervisory Control and Data Acquisition (SCADA) metering, and conversions constants determined by the Resource Entity and provided to ERCOT through the Resource Registration process; | X | X | X | As needed / 2 seconds | As needed / Continuous | ICCP Naming Convention Private WAN point-to-point connection (RTA)/ EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA)
6.5.5.2(2)(c) | Gross Reactive Power (in Megavolt-Amperes reactive (MVAr)); | X | X | X | As needed / 2 seconds | As needed / Continuous | ICCP Naming Convention Private WAN point-to-point connection (RTA)/ EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA)
6.5.5.2(2)(d) | Net Reactive Power (in MVAr); | X | X | X | As needed / 2 seconds | As needed / Continuous | ICCP Naming Convention Private WAN point-to-point connection (RTA)/ EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA)
6.5.5.2(2)(e) | Power to standby transformers serving plant auxiliary Load; | X | X | X | As needed / 10 seconds | As needed / Continuous | ICCP Naming Convention Private WAN point-to-point connection (RTA)/ EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA)
6.5.5.2(2)(f) | Status of switching devices in the plant switchyard not monitored by the TSP or DSP affecting flows on the ERCOT Transmission Grid; | X | X | X | As needed / 10 seconds | As needed / Continuous | ICCP Naming Convention Private WAN point-to-point connection (RTA)/ EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA)
6.5.5.2(2)(h) | Generation Resource breaker and switch status; | X | X | X | As needed / 2 seconds | As needed / Continuous | ICCP Naming Convention Private WAN point-to-point connection (RTA)/ EIP XML or other external app Encrypted via https; authenticated via Digital Certificate (OPA)
6.5.5.2(2)(i) | HSL (Combined Cycle Generation Resources) shall: | Intro | Intro | Intro
6.5.5.2(2)(i)(i) | Submit the HSL of the current operating configuration; and |  | X | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.5.2(2)(i)(ii) | When providing RRS ECRS, update the HSL as needed, to be consistent with Resource performance limitations of RRS ECRS provision; |  |  | X | 2 seconds | As needed | ICCP Naming Convention Private WAN point-to-point connection
6.5.5.2(2)(j) | NFRC currently available (unloaded) and included in the HSL of the Combined Cycle Generation Resource’s current configuration; |  |  | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.5.2(2)(k) | High Emergency Limit (HEL), under Section 6.5.9.2, Failure of the SCED Process; |  |  | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.5.2(2)(l) | Low Emergency Limit (LEL), under Section 6.5.9.2; |  |  | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.5.2(2)(m) | LSL; |  | X | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.5.2(2)(n) | Configuration identification for Combined Cycle Generation Resources; |  |  | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.5.2(2)(o) | Ancillary Service Schedule for each quantity of RRS ECRS and Non-Spin which is equal to the Ancillary Service Resource Responsibility minus the amount of Ancillary Service deployment; |  |  | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.5.2(2)(o)(i) | For On-line Non-Spin, Ancillary Service Schedule shall be set to zero; |  |  | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.5.2(2)(o)(ii) | For Off-Line Non-Spin and for On-Line Non-Spin using Off-Line power augmentation technology the Ancillary Service Schedule shall equal the Non-Spin obligation and then shall be set to zero within 20 minutes following Non-Spin deployment; |  |  | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.5.2(2)(p) | Ancillary Service Resource Responsibility for each quantity of Regulation Up (Reg-Up), Regulation Down (Reg-Down), RRS, ECRS, and Non-Spin. The sum of Ancillary Service Resource Responsibility for all Resources in a QSE is equal to the Ancillary Service Supply Responsibility for that QSE; |  |  | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.5.2(2)(q) | Reg-Up and Reg-Down Services participation factors represent how a QSE is planning to deploy the Ancillary Service energy on a percentage basis to specific qualified Resource(s). The Reg-Up and Reg-Down Services participation factors for a Resource providing Fast Responding Regulation Up Service (FRRS-Up) or Fast Responding Regulation Down Service (FRRS-Down) shall be zero; and |  |  | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.5.2(2)(r) | The designated Master QSE of a Generation Resource that has been split to function as two or more Split Generation Resources shall provide Real-Time telemetry for items (a), (b), (c), (d), (e), (g), and (h) above, PSS and AVR status for the total Generation Resource in addition to the Split Generation Resource the Master QSE represents. |  |  | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.5.2(3) | For each Intermittent Renewable Resource (IRR), the QSE shall set the HSL equal to the current net output capability of the facility. The net output capability should consider the net real power of the IRR generation equipment, IRR generation equipment availability, weather conditions, and whether the IRR net output is being affected by compliance with a SCED Dispatch Instruction. |  | X | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.5.2(4) | For each Aggregate Generation Resource (AGR), the QSE shall telemeter the number of its generators online. |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.5.2(5) | A QSE representing a Load Resource connected to Transmission Facilities or distribution facilities shall provide the following Real-Time data to ERCOT for each Load Resource and ERCOT shall make the data available, in accordance with ERCOT Protocols, NERC standards and policies, and Governmental Authority requirements, to the Load Resource’s host TSP or DSP at the TSP’s or DSP’s expense. The Load Resource’s net real power consumption, Low Power Consumption (LPC) and Maximum Power Consumption (MPC) shall be telemetered to ERCOT using a positive (+) sign convention: | Intro | Intro | Intro
6.5.5.2(5)(a) | Load Resource net real power consumption (in MW); |  | X | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.5.2(5)(c) | Load Resource breaker status, if applicable; |  | X | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.5.2(5)(d) | LPC (in MW); |  | X | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.5.2(5)(e) | MPC (in MW); |  | X | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.5.2(5)(f) | Ancillary Service Schedule (in MW) for each quantity of RRS, ECRS, and Non-Spin, which is equal to the Ancillary Service Resource Responsibility minus the amount of Ancillary Service deployment; |  |  | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.5.2(5)(g) | Ancillary Service Resource Responsibility (in MW) for each quantity of Reg-Up and Reg-Down for Controllable Load Resources, and RRS, ECRS, and Non-Spin for all Load Resources; |  |  | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.5.2(5)(h) | The status of the high-set under-frequency relay, if required for qualification. The under-frequency relay for a Load Resource providing Non-Spin shall be disabled and the status of that relay shall indicate it as disabled or unarmed; |  |  | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.5.2(5)(i) | For a Controllable Load Resource providing Non-Spin, the Scheduled Power Consumption that represents zero Ancillary Service deployments; |  |  | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.5.2(5)(j) | For a single-site Controllable Load Resource with registered maximum Demand response capacity of ten MW or greater, net Reactive Power (in MVAr); |  |  | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.5.2(5)(k) | Resource Status (Resource Status shall be ONRL if high-set under-frequency relay is active); |  |  | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.5.2(5)(l) | Reg-Up and Reg-Down services participation factor, which represents how a QSE is planning to deploy the Ancillary Service energy on a percentage basis to specific qualified Resource(s). The Reg-Up and Reg-Down services participation factors for a Resource providing FRRS-Up or FRRS-Down shall be zero; and |  |  | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.5.2(5)(m) | For a Controllable Load Resource providing Non-Spin, the “Scheduled Power Consumption Plus Two Hours,” representing the QSE’s forecast of the Controllable Load Resource’s instantaneous power consumption for a point two hours in the future. |  |  | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.5.2(7) | A QSE providing any Regulation Service shall provide telemetry indicating the appropriate status of Resources providing Reg-Up or Reg-down, including status indicating whether the Resource is temporarily blocked from receiving Reg-Up and/or Reg-Down deployments from the QSE. This temporary blocking will be indicated by the enabling of the Raise Block Status and/or Lower Block Status telemetry points. |  |  | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.5.2(7)(a) | Raise Block Status and Lower Block Status are telemetry points used in transient unit conditions to communicate to ERCOT that a Resource’s ability to adjust its output has been unexpectedly impaired. |  |  | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.5.2(7)(e) | The Resource limits and Ancillary Service telemetry shall be updated as soon as practicable. Raise Block Status and Lower Block Status will then be disabled. |  |  | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.5.2(9) | Each QSE shall report the current configuration of combined-cycle Resources that it represents to ERCOT. The telemetered Resource Status for a Combined Cycle Generation Resource may only be assigned a Resource Status of OFFNS if no generation units within that Combined Cycle Generation Resource are On-Line. |  |  | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.5.2(10) | A QSE representing Combined Cycle Generation Resources shall provide ERCOT with the possible operating configurations for each power block with accompanying limits. Combined Cycle Train power augmentation methods may be included as part of one or more of the registered Combined Cycle Generation Resource configurations. | X |  |  | various | As needed | Resource Registration Encrypted via https; authenticated via Digital Certificate
6.5.5.2(12) | A QSE representing an Energy Storage Resource (ESR) shall provide the following Real-Time telemetry data to ERCOT for each ESR: |  | Intro | Intro
6.5.5.2(12)(a) | Maximum Operating State of Charge, in MWh; |  | X | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.5.2(12)(b) | Minimum Operating State of Charge, in MWh; |  | X | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.5.2(12)(c) | State of Charge, in MWh; |  | X | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.5.2(12)(d) | Maximum Operating Discharge Power Limit, in MW; and |  | X | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.5.2(12)(e) | Maximum Operating Charge Power Limit, in MW. |  | X | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.7.1.7 | Real-Time Weather and Dynamic Rating Processor | Header | Header | Header
6.5.7.1.12 | Resource Limits | Header | Header | Header
6.5.7.1.12(2)(b)(i) | Normal Ramp Rate based on the values telemetered by the QSE to ERCOT; |  |  | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.7.1.12(2)(b)(ii) | Emergency Ramp Rate based on the values telemetered by the QSE to ERCOT; |  |  | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.7.1.12(2)(b)(iii) | SURAMP, which represents the ability of a Load Resource to decrease consumption in SCED; |  |  | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.7.1.12(2)(b)(iv) | SDRAMP, which represents the ability of a Load Resource to increase consumption in SCED; |  |  | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.7.1.13 | Data Inputs and Outputs for the Real-Time Sequence and SCED | Header | Header | Header
6.5.7.1.13(1) | Inputs: The following information must be provided as inputs to the Real-Time Sequence and SCED. ERCOT may require additional information as required, including: | Intro | Intro | Intro
6.5.7.1.13(1)(a) | Real-Time data from TSPs including status indication for each point if that data element is stale for more than 20 seconds; |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.7.1.13(1)(a)(i) | Transmission Electrical Bus voltages; |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.7.1.13(1)(a)(ii) | MW and MVAr pairs for all transmission lines, transformers, and reactors; |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.7.1.13(1)(a)(iii) | Actual breaker and switch status for all modeled devices; and |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.7.1.13(1)(a)(iv) | Tap position for auto-transformers; |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.7.1.13(1)(c) | Transmission Element ratings from TSPs; | Intro | Intro | Intro
6.5.7.1.13(1)(c) | Data from the Network Operations Model: | Intro | Intro | Intro
6.5.7.1.13(1)(c)(i)(A) | Transmission lines – Normal, Emergency, and 15-Minute Ratings (MVA); and | X | X | X | As needed | At least 3 months prior to the physical equipment changes | ICCP Naming Convention Private WAN point-to-point connection (RTA) / NOMCR Encrypted via https; authenticated via Digital Certificate (OPA)
6.5.7.1.13(1)(c)(i)(A) | Transformers and Auto-transformers – Normal, Emergency, and 15-Minute Ratings (MVA) and tap position limits; | X | X | X | As needed | At least 3 months prior to the physical equipment changes | ICCP Naming Convention Private WAN point-to-point connection (RTA) / NOMCR Encrypted via https; authenticated via Digital Certificate (OPA)
6.5.7.1.13(1)(c)(ii) | Data from QSEs: | Intro | Intro | Intro
6.5.7.1.13(1)(c)(ii)(A) | Generator Step-Up (GSU) transformers tap position; |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.7.1.13(1)(c)(ii)(B) | Resource HSL (from telemetry); and |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.7.1.13(1)(c)(ii)(C) | Resource LSL (from telemetry); and |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.7.1.13(1)(d) | Real-Time weather, from Wind-powered Generation Resources (WGRs), and where available from TSPs or other sources. ERCOT may elect to obtain other sources of weather data and may utilize such information to calculate the dynamic limit of any Transmission Element. |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.7.6.2.3 | Non-Spinning Reserve Service Deployment | Header | Header | Header
6.5.7.6.2.3(8) | For DSRs providing Non-Spin, on deployment of Non-Spin, the DSR’s QSE shall adjust its Resource Output Schedule to reflect the amount of deployment. For non-DSRs with Output Schedules providing Non-Spin, on deployment of Non-Spin, ERCOT shall adjust the Resource Output Schedule for the remainder of the Operating Period to reflect the amount of deployment. ERCOT shall notify the QSEs representing the non-DSR of the adjustment through the MIS Certified Area. |  |  | X | 2 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.7.7 | Voltage Support Service | Header | Header | Header
6.5.7.7(6) | Each interconnecting TSP, or the TSP’s agent, shall telemeter via ICCP the Real-Time Voltage Set Point to ERCOT at the Point of Interconnection Bus (POIB) for each Generation Resource interconnected to the TSP’s system required to provide VSS. Each interconnecting TSP, or the TSP’s agent shall modify the telemetered Voltage Set Point to match any verbal Voltage Set Point instructions as soon as practicable. ERCOT shall telemeter the Real-Time desired Voltage Set Point and the TSP-designated POIB kV measurement via ICCP to each QSE representing a Generation Resource . Each QSE representing a Generation Resource shall provide in Real-Time the desired Voltage Set Point and the associated POIB kV measurement provided by ERCOT to the Resource Entity for that Generation Resource. |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
6.5.9.5 | Block Load Transfers between ERCOT and Non-ERCOT Control Areas | Header | Header | Header
6.5.9.5(1)(h) | SCADA telemetry on switching devices at BLT points that are deemed necessary by ERCOT to be modeled in the Network Operations Model must be provided by the TSP registering the BLT. |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
Provisions for notification of current Protection System and Remedial Action Scheme status or degradation that impacts System reliability.
Section | Operating Guide Language |  |  |  | Periodicity | Deadline | Format & Security Protocol
OG 2.2.5 | Automatic Voltage Regulators | Header | Header | Header
OG 2.2.5(1) | A Resource Entity shall immediately notify their QSEs and its interconnecting TO of any change in Automatic Voltage Regulator (AVR) status (i.e., AVR unavailability due to maintenance or failure and when the AVR returns to normal operation). A QSE shall immediately notify ERCOT, via telemetry and verbal notification of any change in AVR status and shall supply AVR status logs to ERCOT upon request per Protocol Section 6.5.5.1, Changes in Resource Status. For each Generation Resource that is On-Line but not producing real power and is not capable of providing Reactive Power, each QSE must still telemeter its AVR status to ERCOT, but is not required to provide verbal notifications of its AVR status changes to ERCOT during these operating conditions. |  | X | X | As soon as reasonably practicable and 2 seconds | As needed and Continuous | Phone Point-to-point voice communication and ICCP Naming Convention Private WAN point-to-point connection
OG 2.2.6 | Power System Stabilizers | Header | Header | Header
OG 2.2.6 (2) | Resource Entities shall notify their QSEs of any change in PSS status (e.g. PSS unavailability due to maintenance or failure and when the PSS returns to normal operation). QSEs shall notify ERCOT and the TO at the POI of any change in PSS status and shall supply PSS status logs to ERCOT upon request per Protocol Section 6.5.5.1, Changes in Resource Status. |  | X | X | As soon as reasonably practicable and 2 seconds | As needed and Continuous | Phone Point-to-point voice communication and ICCP Naming Convention Private WAN point-to-point connection
OG 2.7.3.3 | TO/TSP Responsibilities | Header | Header | Header
OG 2.7.3.3(4) | Each TO shall telemeter to ERCOT via ICCP the Real-Time desired Voltage Set Point and actual voltage at the POIB for each Generation Resource interconnected to its system required to provide VSS. Each TO shall modify the telemetered Voltage Set Point as soon as practicable in order to match any verbal Voltage Set Point instruction issued. |  |  | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
OG 2.7.3.3(5) | Each TO shall know the status of static transmission Reactive Power resources in its operating area and shall provide such information to ERCOT. |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
OG 2.7.3.4 | QSE Responsibilities
OG 2.7.3.4(4) | Each QSE must, as soon as practicable, notify ERCOT, via telemetry and verbal notifications, when a Generation Resource experiences a change that affects its reactive capability, including any change to the operation mode of the Generation Resource’s AVR. For each Generation Resource that is On-Line but not producing real power and is not capable of providing Reactive Power, each QSE must still telemeter its AVR status to ERCOT, but is not required to provide verbal notifications of its AVR status changes to ERCOT during these operating conditions. |  | X | X | As soon as reasonably practicable and 2 seconds |  | Phone Point-to-point voice communication and ICCP Naming Convention Private WAN point-to-point connection
OG 4.5.3.2 | General Procedures During EEA Operations | Header | Header | Header
OG 4.5.3.2 (1)(f) | QSEs shall report when On-Line or available capacity is at risk due to adverse circumstances; |  |  | X | As soon as reasonably practicable | As needed | Phone Point-to-point voice communication
OG 4.5.3.2 (1)(i) | QSEs shall not remove an On-Line Generation Resource without prior ERCOT authorization unless such actions would violate safety, equipment, or regulatory or statutory requirements. Under these circumstances, QSEs shall immediately inform ERCOT of the need and reason for removing the On-Line Generation Resource from service. |  |  | X | As soon as reasonably practicable | As needed | Phone Point-to-point voice communication
OG 4.5.3.5 | EEA Termination | Header | Header | Header
OG 4.5.3.5(2) | QSEs and TOs shall: | Intro | Intro | Intro
OG 4.5.3.5(2)(c) | Report back to the ERCOT System Operator when each level is accomplished; and |  |  | X | As soon as reasonably practicable | As needed | Phone Point-to-point voice communication
OG 6.2.4 | Protective Relay System Failure Response | Header | Header | Header
OG 6.2.4(4) | The affected QSE or TO shall immediately notify the ERCOT Shift Supervisor via phone call and initiate prompt corrective action. These corrective actions are to address reliability issues for the systems that the QSE and TO monitor and/or operate. |  |  | X | As soon as reasonably practicable | As needed | Phone Point-to-point voice communication
OG 6.2.4(7) | The affected QSE and TO shall promptly notify the ERCOT Shift Supervisor via phone call of the return to service of the previously identified protective relay systems. |  |  | X | As soon as reasonably practicable | As needed | Phone Point-to-point voice communication
OG 11.2 | Remedial Action Schemes | Header | Header | Header
OG 11.2(3)(i) | When a RAS is removed from service, the RAS Entity or its a Designated Agent shall immediately notify ERCOT; | X | X | X | As soon as reasonably practicable | As needed | Phone Point-to-point voice communication
OG 11.2(3)(j) | When a RAS is returned to service, the RAS Entity or its Designated Agent shall immediately notify ERCOT… | X | X | X | As soon as reasonably practicable | As needed | Phone Point-to-point voice communication
OG 11.2(3)(k) | The RAS Entity shall telemeter the status indication of the following items by SCADA to ERCOT for incorporation into ERCOT systems: |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
OG 11.2(3)(k)(i) | Any automatic or manual arming/activation or operation of the RAS; |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
OG 11.2(3)(k)(ii) | The in-service/out-of-service status of the RAS; and |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
OG 11.2(3)(k)(iii) | Any additional related telemetry that already exists pertinent to the monitoring of the RAS (e.g. status indication of communications links between associated RAS equipment and the owner’s control center, arming limits of associated RAS equipment); and |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
OG 11.3 | Automatic Mitigation Plans | Header | Header | Header
OG 11.3 (3)(a) | Immediately notify ERCOT, when an AMP is removed from service and when an AMP is returned to service. ERCOT shall modify its reliability constraints to recognize the availability of the AMP; | X | X | X | As soon as reasonably practicable | As needed | Phone Point-to-point voice communication
OG 11.3 (3)(b) | Telemeter the status indication of the following items by SCADA to ERCOT for incorporation into ERCOT systems | Intro | Intro | Intro
OG 11.3 (3)(b)(i) | Any automatic or manual arming/activation or operation of the AMP; |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
OG 11.3 (3)(b)(ii) | In-service/out-of-service status of the AMP; and |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
OG 11.3 (3)(b)(iii) | Any additional related telemetry that already exists pertinent to the monitoring of the AMP (e.g. status indication of communications links between associated AMP equipment and the owner’s control center, arming limits of associated AMP equipment). |  | X | X | 10 seconds | Continuous | ICCP Naming Convention Private WAN point-to-point connection
Note on F138: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Frosch, Colleen I changed the periodicity cells to state "as needed" due to the language in 3.10.6(3) removing the term "annually". Can you please review if this is ok? Thank you.

## Revision History
Date | Version | Description and Reason for Change | Author(s)
2017-01-01 | 1 | Initial posting | Yvette Landin, ERCOT Staff
2017-07-03 | 2 | Protocol section 3.8.3 and 3.9.1 updated per NPRR272, Section4.4.4 updated per NPRR 818, OG section updated per NOGRR164. Corrections to protocol and OG numbering, corrections to OPA, RTA and RTM columns, corrections to security protocol columns. | Colleen Frosch, ERCOT Staff
2018-01-30 | 3 | Updated Propose tab, updates per NPRR758, added additional section 3.1.5.1, deleted 4.2.2(1), requesting same data as in 3.13(1), deleted 6.5.7.1.7(1), no data request, added intro sections, corrected various columns. | ERCOT compliance staff
2018-12-07 | 4 | Updated Data Requirements tab, updates per NPRR776, NPRR869, NOGRR167and NOGRR174, and added additional Protocol Section 3.10.7.5.2(8), 3.10.7.3(1)(b), and 6.5.7.7(6), added additional Op Guide Sections 2.7.3.3(4) and 2.7.3.3(5), added intro Sections where necessary, and an administrative edit to Protocol Section 6.5.7.1.13(1)(d). | ERCOT compliance staff
2019-08-14 | 5 | Updated Data Requirements tab, to add section 3.10.7.5.1(1) as it was missed in initial posting; updated per NPRR863 and 901. | ERCOT compliance staff
2020-01-31 | 6 | Updated Data Requirment tab per NPRR889, NPRR849, and NPRR957 | ERCOT compliance staff
2020-07-30 | 7 | Fixed typo 6.5.9.5 (1)(h), updates to section 11 per NOGRR164, updates to section 3 per NPRR953 and NPRR1019. Deleted OP 2.7.5, not used for OPA. | ERCOT compliance staff
2021-04-28 | 8 | Fixed typos on rows 77, 91, 99, and 229-231; Updated RARF (series of spreadsheets) to Resource Registration throughout per NPRR1003 Updated 3.15.3 (4) per NPRR 1001 | ERCOT compliance staff
2021-10-28 | 9 | Removed X's on rows 26, 37, 52, 60, 72, 75, 92, 98, 106, 108, 111, 116, 122, 131, 139, 150, 160, 179, 249 and marked as Intro; Removed row 117, 118, & 244 as the data required is already included; Removed row 68; Row 191, 192, 194, 196-211 updated per NPRR979; Removed RTA designation for rows 272, 274-275, 278-280; Added RTA designation for rows 296-300, and 313 Removed langage "to ensure confidentiality and integrity" from Private WAN point-to-point connection throughout | ERCOT compliance staff
2022-04-29 | 10 | Edit to line 30 per NPRR 1087 Added lines 118 (Header) & 119 Protocol 3.10.6(1) Added line 171 Protcol 3.10.7.2(1) Edit to line 171 per NPRR1016 Edit to line 172 due to protocol renumbering Edit to lines 184, 195, & 314 per NPRR1005 Added line 237 Protocol 6.4.6(2)(a) Added line 278 Protocol 6.5.5.2(7) Edit to line 325 per NOGRR212 | ERCOT compliance staff
2023-02-23 | 11 | Edit to line 3 per NPRR 1084 Protocol 3.1.4.4 Edit to line 7 per NPRR 1084 Protocol 3.1.4.5(2) Added line 8 per NPRR 1084 Protocol 3.1.4.5(3) Added line 9 per NPRR 1084 Protocol 3.1.4.5(5) Edit to line 11 per NPRR 1084 Protocol 3.1.4.7(1) Added line 12 per NPRR 1084 Protocol 3.1.4.7(2) Added line 13 per NPRR 1084 Protocol 3.1.4.7(3) Edit to line 19 per NPRR 1108 Protocol 3.1.6.2(1) Edit to line 25 per NPRR 1084 Protocol 3.1.6.2(1)(f) Edit to lines 33 & 34 per NPRR 1093 Protocols 3.6.1(1)(a)(iii) and 3.6.1(1)(a)(iv) respectively Added line 35 per NPRR 1093 Protocol 3.6.1(1)(a)(v) Added lines 74-75 & 131-151 per NPRR1132 Protocol 3.9 and Protocol 3.10.6(3-5) respectively Added line 93 per NPRR 863 Protocol 3.9.1(5)(b)(i)(L) Renumbered lines 94-98 per NPRR 863 Protocols 3.9.1(5)(b)(i)(M-Q) Edit to line 100 per NPRR 1100 Protocol 3.9.1(5)(b)(ii)(A) Edit to line 103 and 104 per NPRR 1100 Protocol 3.9.1(5)(b)(ii)(D) and 3.9.1(5)(b)(ii)(E) respectively Edit to line 110 per NPRR 1093 Protocol 3.9.1(5)(b)(iii)(E) Added lines 111 & 113 per NPRR 863 Protocols 3.9.1(5)(b)(iii)(F) and 3.9.1(5)(b)(iii)(H) respectively Renumbered line 112 per NPRR 863 Protocol 3.9.1(5)(b)(iii)(F) to 3.9.1(5)(b)(iii)(G) Edit to line 123 per NPRR 863 Protocol 3.9.1(5)(g)(iii) Added line 124 per NPRR 863 Protocol 3.9.1(5)(g)(iv) Renumbered line 125 per NPRR 863 Protocol 3.9.1(5)(g)(iv) to 3.9.1(5)(g)(v) Edit to line 180 per NPRR 973 Protocol 3.10.7.1.4 Edit to line 203 per NPRR 973 Protocol 3.10.7.2(1) Edit to line 261 Removed "and ESR", as this is still gray boxed language Edit to line 299 per NPRR 1093 Protocol 6.5.5.2(5)(c) Edit to line 304 per NPRR 1093 Protocol 6.5.5.2(5)(h) Edit to line 344 per NPRR 1093 Protocol 6.5.7.6.2.3(7) was renumbered to 6.5.7.6.2.3(8) | ERCOT compliance staff
2023-11-16 | 12 | Added lines 14, 15, and 16 per NPRR1085 Protocol 3.1.4.7(4), 3.1.4.7(5), 3.1.4.7(6) Edit to line 30 per administrative change, Protocol 3.1.6.11(1) Added line 37 per NPRR863 Protocol 3.6.1(1)(a)(iv) Edit to lines 38 and 39 - Renumbered per NPRR863 Protocol 3.6.1(1)(a)(v) and 3.6.1(1)(a)(vi) Edit to line 75 per NPRR863 Protocol 3.8.3(1) Edit to line 81 per NPRR1085 Protocol 3.9.1(2) Edit to line 102 per NPRR1085 Protocol 3.9.1(5)(b)(i)(Q) Added line 103 per NPRR1085 Protocol 3.9.1(5)(b)(i)(R) Edit to lines 107 and 108 per NPRR1085 Protocol 3.9.1(5)(b)(ii)(C) and 3.9.1(5)(b)(ii)(D) Edit to lines 115, 116, 126, 127 per NPRR1178 Protocol 3.9.1(5)(b)(iii)(E), 3.9.1(5)(b)(iii)(F), 3.9.1(5)(g)(i), 3.9.1(5)(g)(ii) respectively Edit to line 136 per NPRR1132 Protocol 3.10.6(3) Edit to lines 138-139, 141-142, 144-145, 147-148, 150-151, 153-155 per NPRR1132 Protocols 3.10.6(3)(a - b), 3.10.6(4) Added line 156 per NPRR1132 156 Protocol 3.10.6(5) Edit to line 157 - Renumbered per NPRR1132 Protocol 3.10.6(6) Edit to line 217 – Administrative Change due to spelling correction (Model instead of Mondel; each of instead of eachof) Edit to line 229 – Administrative Change due to spelling correction (providing instead of provideing) Edit to line 232 – Administrative Change due to spelling correction (Estimator requirements instead of Estimatorrequirements) Added lines 268-269 per NPRR 1138 Protocol 3.15.3(9) and 3.15.3(9)(d) Edit to line 277 – Administrative Change due to spelling correction (status instead of staus) Added lines 278-285 per NPRR1085 Protocol 6.4.8(1-4) Edit to line 287 per NPRR1085 Protocol 6.5.5.1(1) Added lines 288 and 290 per NPRR1085 Protocol 6.5.5.1(2) and 6.5.5.1(5) Added line 289 per NPRR1161 Protocol 6.5.5.1(3) Edit to lines 302, 308, 311, 321, 322 per NPRR863 Protocol 6.5.5.2(2)(i)(ii), 6.5.5.2(2)(o), 6.5.5.2(2)(p), 6.5.5.2(5)(f), 6.5.5.2(5)(g) Edit to line 369 – Administrative Change due to spelling correction (and Remedial instead of andRemedial) Edit to line 372 per NOGRR246 Operating Guide 2.2.5(1) Added lines 378-379 per NOGRR246 Operating Guide OG 2.7.3.4(4) Edit to line 390 - Administrative Change OG 11.2(3)(i) | ERCOT compliance staff