## Sheet1
MIS SECURE AREA POSTINGS - ECEII
EMIL_ID | PRODUCT NAME | POSTING TYPE | PRODUCT DESCRIPTION | PROTOCOL / GUIDE REFERENCE
NP3-582-ER | KV Residuals - SE vs Telemetry - for Key Buses Report | Report | ERCOT will utilize this report to ensure that for all important voltage buses, telemetered bus voltage minus state estimator voltage falls within the greater of 2% accuracy or the accuracy of the telemetered voltage measurement involved for at least 95% of samples. | NOG9.3.1(1)(d), NP3.10.9, NP3.10.9.2, NP8.2(2)(a)(iii), NP8.2(2)(a)(iv), NP8.2(2)(b)(ix), State Estimator Performance Standards, NP3.10.4(1)
NP6-216-ER | Monthly Average Dynamic Ratings Report | Report | Monthly Summary report to MIS Secure area for each dynamically rated Transmission Element specifying the average change in Normal Rating in MVA that is gained on the element through use of a Dynamic Rating rather than the Normal Rating. Publish Dynamic Rating report | NP6.5.7.1.7(2)
NP8-365 | Monthly Telemetry Point Availability Statistics Report | Report | ERCOT will utilize Monthly Market Participant Real Time Availability Statistics reporting to verify that 92% of all telemetry provided to ERCOT achieves a quarterly availability of 80%. This report will enable ERCOT to evaluate the availability | NOG9.1.3(1)(a)(i), NOG9.2.2(1)(a)(i), NP3.10.7.5.1(2), NP8, NP8.1(3)(a), NP8.3(1)(b)(i), NP8.3(1)(a)(i), NP3.10.7.5.1(5)
NP3-579-ER | MW Residuals - SE vs RTCA Base Case - For Congested Transmission Elements Report | Report | ERCOT will utilize this report to ensure that the residual difference between SE results and Power Flow results for congestion elements is less than 3% of the associated element emergency rating on at least 95% of samples measured in a one month period. | NOG9.3.1(1)(b), NP3.10.9, NP3.10.9.2, NP8.2(2)(a)(iii), State Estimator Performance Standards, NP3.10.4(1)
NP3-581-ER | MW Residuals - SE vs Telemetry for Major Transmission Elements Report | Report | ERCOT will utilize this report to ensure that all SCADA residuals (SE MW SCADA) for all Transmission Elements over 100kV are <10% of emergency rating or <10Mw (whichever is greater) on 99.5% of all samples during a 30 day period. | NOG9.3.1(1)(e), NP3.10.9, NP3.10.9.2, NP8.2(2)(a)(iii), State Estimator Performance Standards, NP3.10.4(1)
NP8-146 | Quarterly Important Telemetry Availability Report | Report | ERCOT will utilize Important Points Violating Quarterly Availability Standards reporting to verify that 92% of important real time measurements (telemetry important for monitoring the important list consist of transmission elements identified as causing 80% of congestion cost for last year, 20 important station voltages, interface components and load ties). | NOG9.2.2(1)(a)(i), NP8.3(1)(b), NP8.3(1)(b)(i), NP8.3(1)(a)(i), OBD Telemetry Standards
NP8-475 | Quarterly Telemetry Point Availability Statistics Report | Report | ERCOT will utilize Quarterly Point Availability Statistics reporting to verify that Each point achieves a quarterly availability of at least 80%. This report will enable ERCOT to evaluate the availability and quality of each telemetered measurement. | NP8.1(3)(a), NOG9.1.3(1)(a)(i)
NP3-580-ER | SE Performance MW Residuals SE vs Telemetry for Congested Transmission Element Reports | Report | In order to analyze congestion and pinpoint possible errors in the network model, ERCOT will utilize this report to identify situations where Congested Transmission Elements are out of compliance (differences between the Mw telemetry values and MW SE values) | NOG9.3.1(1)(c), NP3.10.9, NP3.10.9.2, NP8.2(2)(a)(iii), State Estimator Performance Standards, NP3.10.4(1)
NP3-363-ER | State Estimator Bus Telemetry Accuracy Report | Report | Market Participants will utilize Electrical Buses Not Meeting Accuracy Requirements reporting to evaluate Electrical Buses not meeting Telemetry Accuracy requirements. Sum of flows into any telemetered bus less than the greater of 5 Mw or 5% of the largest line rating at each bus. This reporting will enable ERCOT to track and research quality issues by month throughout 2 years of history. | NP3.10.7.5.2(5), NP3.10.9.2, NP8.2(2)(a)(iii), NOG9.3.1(1)(f)
NP3-217-CD | Forecasted Temperature Adjusted Dynamic Ratings | Report | Dynamic ratings adjusted for the current temperature | NP3.10.8(3), NP3.10.4(1), NP4.2.4.1(1)(a)
NP6-622-CD | Hourly State Estimator Phase Shifter Information | Report | Phase shifter tap and flow information | NP8.2(2)(a)(iii), PUCT25.505(f)(2)€
NP6-215-CD | Real-Time Dynamic Rating Data | Report | ERCOT shall post summaries of dynamically adjusted Transmission Element limits on the MIS Secure Area in a form that allows Market Participants to directly upload Real-Time data into the Common Information Model (CIM). | NP6.5.7.1.7(1)
NP6-93-CD | State Estimator Switch Status | Report | Data Inputs and Outputs for the Real-Time Sequence and SCED. Status of all breakers and switches used in the Network Security Analysis except breakers and switches connecting Resources to the ERCOT Transmission Grid | NP6.5.7.1.13(4)(a)
NP6-291-CD | Topology Consistency | Report | Topology Consistency Analyzer. Publish output from Topology Consistency Analyzer summaries of incorrect breaker and switch statuses | NP6.5.7.1.5
NP6-627-CD | State Estimator Bus Voltages | Report | Posting of the state estimator bus voltage results for each hour | PUC Substantive Rule §25.505, PUCT25.505(f)(2)(E)
NP6-619-CD | State Estimator Real-Time Transmission Line Flows | Report | Redacted set of SE transmission flow information | PUCT25.505(f)(2)(E)
NP3-772-M | TSP Rating Methodology | Document | ERCOT shall post all methodologies on the MIS Secure Area within seven days following a change in methodology | NP3.10(3)
NP3-459-SG | Network Operations Model Interim Update Report | Report | Interim updates detailing the changed model information and the reason for the interim update | NOG9.3.5, NP3.10.4(7)
NP6-584-ER | Security Violations and Binding Transmission Constraints | Report | Security Constrained Economic Dispatch. Post Security Violations and Binding Transmission Constraints | NP6.5.7.3(10)(c)
NP3-59-M | Approved Constraint Management Plans (CMPs) | Report | Posting of Approved Constraint Management Plans (CMPs) (previous link name - Approved Remedial Action Plans (RAPS)). | NP3.10.7.4(3)