OPERATING GUIDE

Appendix A

Document #OPG00A

Reports and Forms

Version 1.0Contents

A.	Reports and Forms	A-3

A.1	Document Control	A-3

A.2	Reports	A-4

A.2.1	Disturbance Report	A-4

A.2.2	Relay Misoperation Report	A-5

A.2.3	Interruptible Load Used As Capability Verification Procedure	A-6

A.3	Forms	A-7

A.3.1	Turbine Governor Speed Regulation Tests	A-7

A.3.2	Unit Real Power Capability Verification	A-14

A.3.3	Unit Reactive Limits Verification	A-15

A.3.4	Hydro Responsive Reserve Capability Verification	A-16

A.3.5	Off-Line Unit Quick Start (10 Minutes) Capability Verification	A-17

# Reports and Forms

## Document Control

Authorities

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| E. Irwin | Technical Writer | December 29, 2000 |

| Reviewed by | Role | Date Authorized |
| --- | --- | --- |
| B. Garza | Chair – Joint Operating Guide Working Group |  |

Distribution List

| Name | Organization |
| --- | --- |
| Operating Guide Working Group | ERCOT |
| Operations | ERCOT |
| Technical Advisory Committee | ERCOT |
| Reliability Operations Subcommittee | Technical Advisory Committee |

Change History

| Issue/Draft | Reason for issue | Date |
| --- | --- | --- |
| Version 0.1 | Draft for Review | December 29, 2000 |
| Version 0.2 | Not Issued |  |
| Version 0.3 | Include comments from seminar | January 19, 2001 |
| Version 0.4 | Include comments from second seminar | February 5, 2001 |
| Version 1.0 | Updated from Working Group comments. Submitted to Technical Advisory Committee to approve handover to the Reliability Operating Subcommittee | February 28, 2001 |

## Reports

### Disturbance Report

#### ERCOT Data

ERCOT will record the following data when frequency deviations of 0.175 Hz or greater occur and will use this information to generate the ERCOT initial Disturbance Report:

- Net interchange (MW) immediately before the disturbance.

- Net interchange (MW) immediately after the disturbance.

- Control Bias.

- Net MW Capability (including any capability lost) at the time of the disturbance.

- Net System Load (MW) for the hour ending closest to the time of the disturbance.

- Scheduled Net Interchange (MW) at the time of the disturbance.

- Amount of interruptible load (MW) tripped.

#### PGC Data

The PGC losing the unit will provide the following data to the ERCOT Operator as soon as possible after the disturbance:

- Unit Lost.

- Released net dependable capability (MW).

- Net generation at time of loss.

- Nature of trouble/Reason for loss.

- Time/Date of loss.

The above information, plus unit performance data, will be used by ERCOT to generate detailed reports for the PDC Task Force and will be submitted to the PDC Task Force at the next regularly scheduled meeting.

### Relay Misoperation Report

| DATE : | TIME: | UTILITY: | VOLTAGE: |
| --- | --- | --- | --- |
| RELAY TYPE: STYLE #: | CB NUMBER: | LINE/BUS/AUTO NAME: |  |
| FLAGS: | MANUFACTURER: |  |  |
| Description of Misoperation/Failure: |  |  |  |
| (80 Character) |  |  |  |
| Investigation Results: |  |  |  |
| (80 Character) |  |  |  |
| Corrective Action: |  |  |  |
| (80 Character) |  |  |  |
| Target Date: |  |  |  |
| Recommendations: |  |  |  |
| Reported By: |  |  | Date: |
| Phone Number: |  |  |  |

### Interruptible Load Used As Capability Verification Procedure

Interruptible loads used either as Responsive Reserve Service, Supplemental Reserve, or for Automatic Backup shall be verified by the QSE operator as directed by the Control Area Authority in order to minimize the impact on system reliability.  Verification will be made at least annually, except when the capability of the load to be interrupted has been verified through response in an actual event.  If the load is under the direct control of a Control Area Operator via a SCADA system, annual verification shall consist of a test of the relay function with no actual interruption of load.

Specific loads to be used for the first time as capability in reserve calculations must be correctly verified (tripped) prior to their application.  Notice of an Entity’s intent to use a specific load as Responsive Reserve Service, Supplemental Reserve, or for Automatic Backup will be provided to the Control Area Authority.  At a time selected by the Control Area Authority, the QSE Operator shall be notified of the need to verify that interruptible loads used as Responsive Reserve Service can be removed within 20 cycles or that interruptible loads used as Supplemental Reserve or for Automatic Backup can be taken off line within a 10-minute period.  The QSE Operator will immediately initiate the interruption up to the amount being used for Reserve Service and record the following information for each load interrupted:

Type of Reserve Service use:

The name of Specific Load Interrupted:

Start Time:

Start MW:

MW After 10-Minute Notice:

Time to Reach Maximum Interruption:

Limiting Factors:

## Forms

### Turbine Governor Speed Regulation Tests

#### Turbine Governor Speed Regulation Test for Mechanical-Hydraulic Governor

PLANT ______________________	UNIT NO. ___________

Steady State Speed Regulation at High-Speed Stop

Rs=A−B×1003600

Where:

A =	Speed with speed changer set at high-speed stop and with throttle (or stop) valves open and machine running idle on the governor.

B =	Speed with speed changer set at high-speed stop and when governing valves just reach wide-open position.

Steady State Speed Regulation at Synchronous Speed

Rs=C−D×1003600

Where:

C =	Speed with speed changer set for synchronous speed and with throttle (or stop) valves open and machine running idle on the governor.

D =	Speed with speed changer set at the same position as in C above and when governing valves just reach wide open position.

Steady State Speed Regulation at Low-Speed Stop

Rs=E−F×1003600

Where:

E =	Speed with speed changer set at low-speed stop and with throttle (or stop) valves open and machine running idle on the governor.

F =	Speed with speed changer set at low-speed stop and when governing valves just reach wide-open position.

E, F @ Low Speed Stop

C, D @ Sync. Speed

A, B @ High Speed Stop

Test Data

| Point | A | B | C | D | E | F |
| --- | --- | --- | --- | --- | --- | --- |
| Speed, RPM |  |  |  |  |  |  |
| Frequency Hz |  |  |  |  |  |  |

Speed Changer Travel Time:

a.	From Low-Speed Stop to High-Speed Stop in _________seconds.

b.	From High-Speed Stop to Low-Speed Stop in _________seconds.

Over-speed Trip Test Speed at _________rpm.

Comments:

Signed:_______________________________Date:_______________

#### Example of a Turbine Governor Speed Regulation Test for Mechanical-Hydraulic Governor

PLANT ___________Texas___________	UNIT NO. 		1

Steady State Speed Regulation at High-Speed Stop

Rs=A−B×1003600=3850−3570×1003600=7.78%

Where:

A =	Speed with speed changer set at high-speed stop and with throttle (or stop) valves open and machine running idle on the governor.

B =	Speed with speed changer set at high-speed stop and when governing valves just reach wide-open position.

Steady State Speed Regulation at Synchronous Speed

Rs=C−D×1003600=3600−3310×1003600=8.06%

Where:

C =	Speed with speed changer set for synchronous speed and with throttle (or stop) valves open and machine running idle on the governor.

D =	Speed with speed changer set at the same position as in C above and when governing valves just reach wide open position.

Steady State Speed Regulation at Low-Speed Stop

Rs=E−F×1003600=3500−3210×1003600=8.06%

Where:

E =	Speed with speed changer set at low-speed stop and with throttle (or stop) valves open and machine running idle on the governor.

F =	Speed with speed changer set at low-speed stop and when governing valves just reach wide-open position.

E, F @ Low Speed Stop

C, D @ Sync. Speed

A, B @ High Speed Stop

Test Data

| Point | A | B | C | D | E | F |
| --- | --- | --- | --- | --- | --- | --- |
| Speed, RPM | 3850 | 3570 | 3600 | 3310 | 3500 | 3210 |
| Frequency Hz | 64.2 | 59.5 | 60.0 | 55.0 | 58.3 | 53.5 |

Speed Changer Travel Time:

a.	From Low-Speed Stop to High-Speed Stop in 	73	seconds.

b.	From High-Speed Stop to Low-Speed Stop in 	74	seconds.

Over-speed Trip Test Speed at 	3965	rpm.

Comments:

Signed:_______________________________Date:_______________

#### Turbine Governor Speed Regulation Test for Electro-Hydraulic Governor

PLANT __________________________  UNIT NO. ________

Turbine Governor Speed Regulation Test Procedures

- Simulate unit on line and turbine speed at 3600 RPM.

- Set load reference at minimum value.

- Monitor valve demand signal and record as value 'A' (in %).

- Reduce speed until valve demand just reaches maximum value.      Record valve demand as value 'B' (in %) and speed as value 'C' (in RPM).

- Set speed at 3600 and load reference at maximum value.

- Monitor valve demand signal and record as value 'D' (in %).

- Increase speed until valve demand just reaches minimum value.     Record valve demand as value 'E' (in %) and speed as value 'F' (in RPM).

Turbine Governor Speed Regulation Test Results

|  | A | B | C | D | E | F |
| --- | --- | --- | --- | --- | --- | --- |
| Valve Demand (%) |  |  |  |  |  |  |
| Speed (rpm) |  |  |  |  |  |  |

Speed Regulation With Decreasing Speed

RD=100B−A×3600−C3600×100

Speed Regulation With Increasing Speed

RI=100D−E×F−36003600×100

Comments:

Signed  _________________________________  Date __________________________

#### Definitions

| System Frequency Response | This response is a function of three key variables; the system's composite governor droop, the percent of spinning capacity which is actually providing governor response, and the frequency response characteristic of the connected load. |
| --- | --- |
| Percent Droop Settings | Also known as Frequency Regulation, Speed Regulation, Speed Sensitivity, Speed Error and others. Percent droop is the percent change in nominal frequency that will cause generator output to change from no load to full load. It is the change in steady state rotor speed, expressed in percent of rated speed, when power output is gradually reduced from rated to zero power. A common percent droop setting is 5% for both high and low frequency excursions. |
| Dead Band | The range of deviations of system frequency (+/-) that produces no turbine governor response, and therefore, no frequency (speed) regulation. It is expressed in percent of rated speed, Hz, or RPM. |
| Valve Position Limiter | A device that acts on the speed and load governing system to prevent the governor-controlled valves from opening beyond a pre-set limit. |
| Blocked Governor Operation | Operating the generating unit with the control system adjusted to prevent the turbine governor from responding to system frequency (speed) variations. In an effort to reduce speed governor operation in some generating units, turbine control systems can be adjusted to block the operation of the governor after the unit is in parallel with the system and is running at its desired output. Selection of a high percent droop characteristic or a large dead band constitutes a form of blocked governor action. |
| Variable Pressure Operation | Varying the boiler pressure to improve turbine efficiency at lower loads. Two methods are normally used. With one method, the turbine governor (G.E.) or control (Westinghouse) valves are positioned in the wide-open position and the generator is changed by changing the boiler pressure. With this method, there is very little, if any response to frequency excursions. With the other method, the valves are positioned at approximately 50% open. The valves are still able to respond to system disturbances. Normal changes in generation requirements are made by varying the boiler pressure until the unit is at rated pressure. After full pressure is reached, the turbine valves are used to make the required generation changes. |

### Unit Real Power Capability Verification

Date:

Control Area:  		Generation Entity:  			Unit Name:

Start Time:  				Start MW:

MW 10 Minutes after Start Time:  		Time to Reach Maximum Generation:

Temperature at Plant (F):  			MW at Maximum Generation:

MWH Net during the First Full Clock Hour after Maximum Generation is Reached:

Limiting Factors:

Gen. Ent. Rep.:  			Control Area Rep.:  			Control Area Authority Rep.:

### Unit Reactive Limits Verification

Unit Name:  					Date of test:

Host Control Area:  				Generation Entity:

| Instructions | Maximum lagging reactive tests should be performed with the unit at its net dependable MW capability. Leading reactive tests are to be performed during light load conditions of the ERCOT System. Maximum lagging reactive tests are to be performed during ERCOT System high load conditions. This form is to be submitted with a copy of the generator reactive design curve, marking the measured maximum output. Inability to reach the design limit must be noted with an explanation of the limiting factor, which prevented design performance. Verify that the automatic voltage regulator is in service. Minimum acceptable test duration is 15 minutes. The normally specified switchyard voltage should be maintained by adjusting voltage control devices/units in so far as possible. Show leading reactive value as a negative (-) number. |
| --- | --- |

Test Performed:				Location at which data observed:

 Leading Reactive			 Generator Terminals (preferred)

 Maximum Lagging Reactive		 High Voltage side of Generator Step-Up (GSU) Transformer

 Other (specify location):

TESTED REACTIVE CAPABILITY

Generator Gross Reactive (MVAR): (+/-) _____	Net Reactive to System (MVAR): (+/-) _____

Auxiliary Reactive Load (MVAR): _____ (if available)

TEST CONDITIONS:

Start Time: ________________Stop Time: ______________

Generator Gross Generation (MW): _____	Net Dependable Unit Generation (MW): _____

Auxiliary Load (MW): _____			Power Factor: _____

Transmission Bus Voltage (kV): _____	Nominal Transmission Bus Voltage (kV): _____

Generator Terminal Voltage (kV): _____	Auxiliary Bus Voltage (kV): _____ (if limiting)

Ambient Air Temperature (°F): _____

Generator Hydrogen Pressure (psi): _____

Generator Step Up transformer tap setting: ______      Ratio: HV __________kV/ LV ________kV

Abnormal Conditions at Time of Test:

Factors that Limited Reactive Capability During Test:

 Maximum Generator Voltage with Auxiliary loads		 Steady State Stability Limit

 Maximum Generator Voltage without Auxiliary loads	 Maximum Gross MW capability

 Minimum Generator Voltage with Auxiliary loads		 Minimum Gross MW capability

 Minimum Generator Voltage without Auxiliary loads	 Minimum Excitation Limiter

 Main transformer capability plus Auxiliary loads		 Loss of Field Relay

 Other:

Generation Entity Representative:  		 Control Area Representative:

Date submitted to Control Area Authority Rep.:

Notes:	1.  Leading and Maximum Lagging tests may be conducted at different times of the year.

### Hydro Responsive Reserve Capability Verification

Date ______________

Control Area 			Generation Entity 			Unit Name

Date of Test  			Start Time

Start MW 			MW at 4 seconds 			MW at 10 seconds

Max MW 			Gen. Ent. Rep

Control Area Rep 				Control Area Authority Rep

### Off-Line Unit Quick Start (10 Minutes) Capability Verification

Date __________________

Control Area 			Generation Entity 			Unit Name

Date of Test 			Start Time

MW at 10 Minutes

Start- Up Method:		[    ]	Plant Operator:		[    ]	Remote Control

Gen. Ent. Rep.				Control Area Rep

Control Area Authority Rep

Westinghouse recommends using only this test.

Westinghouse recommends using only this test.