Eugene G. Preston, PhD, PE

Transmission Adequacy Consulting

4710 Fawn Run

Austin, Texas 78735

To: 		ERCOT Planning Assessment and Review Working Group

Date:		January 5, 2001

Subject: 	ERCOT Generation and Transmission Reliability Study

Summary of Findings:

- Phase I for 2000 and Phase II for 2003 have similar reliability indices for the same reserve margin percentages.  Both of these no-transmission-constraint studies indicate that the 15% planning reserve margin is reasonable.  The no-load-forecast-uncertainty study has a 13% margin for 0.1 days per year LOLE whereas the 5% load-forecast- uncertainty study has a reserve margin of 20% for 0.1 days per year LOLE.

- Phase III finds that transmission constraints play a major role in creating additional LOLE.  The following are Phase III findings:

  - Base case overloads create significant LOLE at high ERCOT load levels.

  - Contingency case circuit overloads add to the LOLE at lower load levels.

The following pages give the detailed findings of this study under categories Phase I, Phase II, and Phase III.  Computational processes are described, sources of data are given, and references to computer output reports are made in this report.  This report and the associated computer files are posted at http://k5gp.home.texas.net/relstudy.htm.

Please call me or e-mail me if you have any questions.

Sincerely,

Eugene G. Preston

g.preston@ieee.org

512-892-3621 office

512-750-6417 cell

512-891-8045 fax

ERCOT Generation and Transmission Reliability Study

Purpose:

To ensure the reliability and adequacy of the regional electrical network.

Study Phases:

Phase I

Provides a correlation between ERCOT reserve level and reliability indices for the year 2000 for no transmission constraints.

Phase II

Establishs the sensitivity of reliability indices with respect to future ERCOT generation additions through the year 2003 for no transmission constraints.

Phase III

Examines the sensitivity of the year 2003 ERCOT reliability indices to transmission constraints.

Study Assumptions:

- Phase I uses 1998 and 1999 ERCOT hourly load profiles for May – September.

- Phases II and III uses the 1999 hourly load profile.

- Phases I and II are studied with and without a 5% load forecast uncertainty.

- Phases I and II are based on serving firm load.

- Phase III models all loads that are in the 2003 load flow (by necessity) and calculates LOLE, EUE, and reserve margins based on serving firm load.

- Generator outages are random and independent.

- Typical generator forced outage rates are determined using NERC GADS data.

- No generator maintenance is scheduled.

- HVDC and regionally switchable units are 100% available to ERCOT.

- Reserve level calculations do not include self serve and wind generators.

- Phases I and II assume no transmission limitations (single area).

- Phase III uses representative circuit and transformer outage rates.

- Phase III generation loss of load is applied to each bus in proportion to bus load.

- Phase III transmission loss of load is minimized and is assigned to load areas that create the highest circuit flows contributing to transmission overloading.

Phase I

The following tasks are performed in Phase I:

- Nine single area 2000 studies use the 1998 hourly ERCOT loads for months May through September with reserve levels from 5% to 25%.

- Nine additional studies use 1999 hourly loads for May – September.

- Reliability indices are calculated and graphed for the 18 studies.

- Load forecast uncertainty is calculated automatically by the computer program; therefore, the Phase II load uncertainty indices are also calculated and graphed.

- A sensitivity study that investigates the reliability value of wind generation relative to combined-cycle generation is performed.

The generator forced outage rates for various classes of generators that were derived from NERC GADS data and used in this study are:

FOR   DFOR   DER%  GENERATOR TYPE

.0001  .0     0.0   DC - DC TIE

.0422  .029   19.   ST - FOSSIL-STEAM (Western Coal and Lignite)

.067   .0     0.0   ST - FOSSIL-STEAM (Natural Gas)

.069   .023   5.5   NU - NUCLEAR

.10    .0     0.0   CT - COMBUSTION TURBINE

.12    .0     0.0   DI - DIESEL

.56    .0     0.0   HY - HYDRO

.64    .0     0.0   WI – WIND

FOR  = per unit forced outage rate, i.e. the per unit amount of time the unit is in the down state

DFOR = p.u. derated outage rate, i.e. the per unit amount of time the unit is in the derated state

DER% = percent of the unit MW capability that is derated, i.e. the percent reduction in MW output

The wind FOR was estimated based on wind generator data from industry publications and transmission entities for the amount of wind energy produced during the study months without consideration for whether the wind generation is coincident or not coincident with ERCOT loads..

Hydro FOR is derived from NERC data based on the amount of energy that is produced from a large number of small hydro units scattered across the United States.  Hydro generation is very reliable for short run periods.  The high FOR of 56% for hydro that is used in this study accounts for the inability of hydro in Texas to supply energy for extended periods during summer months.

The Phase I study assumes no generator maintenance and no transmission constraints for the summer period months of May through September, a period of 3672 hours per year.

The load forecast uncertainty assumes a normal distribution with 5% of the forecast as one standard deviation.  Load uncertainty is modeled as 101 steps from –4 to +6 standard deviations; i.e. –20% to +30% of the forecasted hourly loads.

Phase I Results:

Generation reliability studies performed for ERCOT in the 1970’s (1970, 1974, and 1978) all calculated LOLE using daily peak loads.  The graph below shows the LOLE results for this study for meeting daily peak loads with and without load forecast uncertainty and for 1998 and 1999 hourly load shapes.

The 1978 study established a benchmark acceptable LOLE of 0.121 days per year by calculating ERCOT’s LOLE assuming a 15% installed reserve margin in 1974.  This benchmark is very close to the standard of 0.10 days per year that has been used by the industry since the 1960s.  In the above graph, ~13% reserve is needed to achieve an LOLE of .1 days per year for no load uncertainty.

The 1978 study also included a sensitivity study to examine the effect of a 5% load uncertainty which showed that a 22.5% reserve would have been needed in 1974 to achieve the same LOLE as a 15% reserve with no load uncertainty.  The graph above shows that when a 5% load forecast uncertainty is added to this study,  ~20% reserve is needed to achieve the .1 days per year LOLE.  The addition of load uncertainty increased the planning reserve requirement by about 7% in both the 1978 study and this study.

Phase I Sensitivity Study:

A year 2000 sensitivity study has been performed in which the four 280 MW combined cycle Midlothian units (1120 MW) are increased in forced outage rate while the MW capability is also increased to hold reliability indices for ERCOT at a constant level.  This allows us to identify the amount of additional capacity needed to overcome a high forced outage rate.  Or, it can be used to derate high FOR units to a lower equivalent MW capability.

The base FOR for the four Midlothian units is 10%.  Although the Midlothian units have been selected to be varied in FOR and MW, the actual intent here is to identify a derating factor that might possibly be used for high FOR wind generation.

The 15% generation reserve load level and 1998 hourly loads were used in this analysis.  The 280 MW for each unit is increased to the following MW when the FOR is set to 64% (wind FOR):

- 280 MW increased to 1426 MW to hold constant the .007692 annual probability for loss of load with no forecast uncertainty

- 280 MW increased to 1630 MW to hold constant the .009316 LOLE for daily peak loads and no forecast uncertainty

- 280 MW increased to 2000 MW to hold constant the .000679 LOLE for hourly loads and no forecast uncertainty

- 280 MW increased to 800 MW to hold constant the .33210957 annual probability for loss of load with 5% load forecast uncertainty

- 280 MW increased to 820 MW to hold constant the .919930 LOLE for daily peak loads and 5% load forecast uncertainty

- 280 MW increased to 820 MW to hold constant the .111253 LOLE for hourly loads and 5% load forecast uncertainty

Using 2), the LOLE index reference with no load uncertainty, the effective capacity of wind is found to be 17% of the wind unit net capability.  Expressed another way, the addition of 100 MW of wind generation or 17 MW of combined-cycle gas generation would have about the same inpact on ERCOT LOLE.  This is based on the simplistic data used to model wind generation.  More detailed time of day wind generation information, and its coincidence with ERCOT load patterns, could raise or lower this value.

Phase II

The following tasks are performed in Phase II:

- Reliability indices are calculated for new generation added after 2000 in 25% steps.  Phase II uses the 2003 firm load forecast of 63315 MW, 1999 hourly loads for May – September, forced outage rates as in Phase I, and no transmission constraints.

- Indices for a load forecast uncertainty of 5% are also calculated.

The graph below shows the LOLE results for Phase II for meeting the 2003 daily peak loads using the 1999 hourly load profile with and without load forecast uncertainty.

These results are very similar to Phase I.  In the above graph, 12.5% reserve level has an LOLE of .1 days per year for no load uncertainty and 20% when a 5% load forecast uncertainty is included.

Assuming wind effective capacity is below 20% shows that the total wind generation of 1711 MW in the 2003 data has little effect on the ERCOT LOLE.  The ERCOT CDR assumes zero MW effective wind capacity in the reserve calculation.

Phase III

The following tasks are performed in Phase III:

- Reliability indices are calculated using the same set of 2003 generators as were used in the Phase II study.  Transmission constraints are included in the Phase III study.

- Typical transmission forced outage rates are developed and used on all circuits.

- Limiting circuits, their associated contingencies, affected load areas, and affected generators are listed.

- Zones in the 2003 load flow data are clustered together to create logical load shedding areas in the load flow data.  The process used to perform this clustering is described.

- Although load forecast uncertainty is not explicitly modeled, the LOLE reliability index is calculated and displayed for a wide range of annual peak demand forecasts.

- The methodology for calculating probabilistic circuit flows based on random generator and circuit outages and how load shedding is performed is described.

The graph below shows the 2003 ERCOT LOLE due to transmission constraints for 100% of the planned generation additions.  The generation LOLE (black) includes 1711 MW wind generation and 920 MW of DC tie capacity.  345 kV constraints are dotted.

The graph below shows the 2003 ERCOT LOLE due to transmission constraints for 100% of the planned generation additions and ten 345 kV circuit upgrades.  The circuits that are upgraded to 1631 MVA are listed as base case overloads in file XXOP3.  Search for overload: and also in the highest loaded summary table in XXOP3.  The circuits are:

1050   6235  ENRONIPP 345  ABMULCW7 345 1   717 MVA

1421   1436  WILLOWCK 345  PARKER   345 1  1072 MVA

1425   6100  FISHRDSS 345  OKLAEHV7 345 1   717 MVA

1436   1859  PARKER   345  EAGLE MT 345 1  1195 MVA

1695   5925  MOSES    345  DC-EAST  345 1   600 MVA

1876   1880  WLFHOL   345  ROCKY CK 345 1  1072 MVA

1907   1911  VENUS N  345  WEBB 1   345 1  1072 MVA

1911   1916  WEBB 1   345  LIG2 T   345 1  1072 MVA

2410   2420  NORWOODT 345  C HILL   345 1  1133 MVA

5915  44000  SO TEX 5 345  W_A_P_ 5 345 39  906 MVA

The upgrades show a dramatic improvement in the transmission base case LOLE (the blue lines with no 345 kV circuits out of service) and very little improvement for the N-3 transmission LOLE (red lines).  This suggests that additional circuits may improve reliability more than upgrading existing ones.  Additional study is needed to verify this.

The graph below shows the 2003 ERCOT LOLE due to transmission constraints for 50% of the capacity of the planned generation additions.  The transmission LOLE is indicative of ERCOT load levels where one or more of the individual load areas are likely to have loss of load due to transmission contingencies.  The black curve is generation only, the blue curve is transmission LOLE for the base case, and the red curve is the base case plus circuit outage cases.  The dotted line cases are 345 kV limiting circuits only.

Below are the top five limiting 345 kV circuits in the N-0 base case from file XXOP0:

CIRCIUT-GENERATOR-AREA LOAD SHEDDING REPORT:

BUS#   BUS NAME      BUS#   BUS NAME   ID       MW        MWH      GENERATOR > LOAD AREA    PDF

1907 VENUS N  345 -  1911 WEBB 1   345 1       280.   148.918091    MELP 3      DFW&NTX   0.23146

5915 SO TEX 5 345 - 44000 W_A_P_ 5 345 39     1311.   147.516998    STP1        HLP       0.27671

2436 TRICOR E 345 -  2437 FORNEY   345 1       189.     3.879349    CALFRE1G    DFW&NTX   0.13912

1421 WILLOWCK 345 -  1436 PARKER   345 1       268.     3.533287    WCPP 3 G    SYSTEM    0.69959

5915 SO TEX 5 345 - 42500 DOW345 5 345 18     1311.     3.425071    STP1        HLP       0.23691

Venus-Webb is loaded to 123.9% in the initial load flow, SoTex-WAP to 111.9%, and Tricor-Forney to 92.7%.  The above circuits cause loss of load in the no circuits out case (base case) for high ERCOT load levels.  Random generator outages can cause higher probabilistic overloads on circuits.  Graphs of the probabilistic circuit flows for these three circuits are shown on the next page.  The circuit overload regions are shown in yellow.

Limiting 345 kV circuits in the N-0 base case from file XXOP0:

The following is a list of all the limiting 345 kV circuits in file XXOP3 (N-3 analysis):

BUS#   BUS NAME      BUS#   BUS NAME   ID       MW        MWH      GENERATOR > LOAD AREA    PDF

1907 VENUS N  345 -  1911 WEBB 1   345 1       280.   154.168915    MELP 3      DFW&NTX   0.23146

5915 SO TEX 5 345 - 44000 W_A_P_ 5 345 39     1311.   149.923859    STP1        HLP       0.27671

2436 TRICOR E 345 -  2437 FORNEY   345 1       189.     4.469209    CALFRE1G    DFW&NTX   0.13912

1421 WILLOWCK 345 -  1436 PARKER   345 1       268.     3.798968    WCPP 3 G    SYSTEM    0.69959

5915 SO TEX 5 345 - 42500 DOW345 5 345 18     1311.     3.477435    STP1        HLP       0.23691

1425 FISHRDSS 345 -  6100 OKLAEHV7 345 1       615.     2.043899    OKLAUN1G    W FALLS   0.65948

2410 NORWOODT 345 -  2420 C HILL   345 1       818.     1.608480    THSE 2 G    DFW&NTX   0.10150

1876 WLFHOL   345 -  1880 ROCKY CK 345 1       468.     0.326960    WLFHOL2G    SYSTEM    0.30760

1885 EVER 1BT 345 -  1933 KENNDLE2 345 1       818.     0.319578    DEC  1 G    DFW&NTX   0.14292

1436 PARKER   345 -  1859 EAGLE MT 345 1       268.     0.274721    WCPP 3 G    DFW&NTX   0.28738

1050 ENRONIPP 345 -  6235 ABMULCW7 345 1       400.     0.253744    ENRONIPP    ABILENE   0.59963

1873 BENBRK   345 -  1890 DECORDVA 345 1       615.     0.156089    DEC  1 G    W FALLS   0.39665

1911 WEBB 1   345 -  1916 LIG2 T   345 1       280.     0.155807    MELP 3      DFW&NTX   0.22870

3429 SANDOW   345 -  7040 AUSTRO34 345 1       167.     0.089803    LOSTPN 3    WACO-CTX  0.27977

1430 GRAHAM   345 -  1436 PARKER   345 1       399.     0.034238    GRAM 2 G    SYSTEM    0.40562

1690 VALLEY   345 -  1692 PARIS SS 345 1       341.     0.033445    LPP 6  G    SYSTEM    0.49176

1906 VENUS S  345 -  2420 C HILL   345 1       280.     0.028497    MELP 2      DFW&NTX   0.36147

5915 SO TEX 5 345 - 42500 DOW345 5 345 27     1311.     0.024837    STP1        HLP       0.23691

3429 SANDOW   345 -  7040 AUSTRO34 345 2       167.     0.020055    LOSTPN 3    WACO-CTX  0.27977

1026 ODES EHV 345 -  1028 ODEHV 1T 345 1       180.     0.019726    TIE ST2G    SYSTEM    0.61476

1917 SHERRY T 345 -  2420 C HILL   345 1       227.     0.014767    DEC  1 G    PALESTIN  0.20326

42000 P_H_R_ 5 345 - 42500 DOW345 5 345 99      986.     0.009747    DOW1        HLP       0.29258

5371 SKYLINE  345 -  7044 MARION34 345 1       155.     0.008193    GUALUP 4    CPS       0.43579

2427 WATMILLW 345 -  2436 TRICOR E 345 1       510.     0.008053    STRYK 2G    VENUS     0.23582

1025 FS COGEN 345 -  1030 MRGN CRK 345 1        70.     0.006933    CALENG2G    SYSTEM    0.85737

3124 TRINDAD2 345 -  3134 RICHLND2 345 1       189.     0.005379    CALFRE6G    DFW&NTX   0.32182

2436 TRICOR E 345 -  3123 TRINDAD1 345 1       189.     0.005338    CALFRE1G    DFW&NTX   0.20812

1436 PARKER   345 -  1869 BENB A T 345 1       268.     0.004348    WCPP 3 G    SYSTEM    0.42769

2432 TRICORN  345 -  2433 SGVL SS  345 1       417.     0.003940    GATEWY4G    DFW&NTX   0.11606

1880 ROCKY CK 345 -  1886 EV EAST  345 1       304.     0.003722    WLFHOL2G    SYSTEM    0.29079

1695 MOSES    345 -  1697 SULSP SS 345 1       227.     0.003654    MOSES2 G    SYSTEM    0.38880

967 GIBCRK B 345 - 44500 OBRIEN 5 345 1       462.     0.003012    GIBCRK      HLP       0.31563

1430 GRAHAM   345 -  6230 ABMULCE7 345 1       615.     0.002795    OKLAUN1G    W FALLS   0.38452

44000 W_A_P_ 5 345 - 44650 SMTHRS 5 345 50      636.     0.002491    WAP6        HLP       0.31607

1886 EV EAST  345 -  1932 KENNDLE1 345 1       818.     0.002259    DEC  1 G    DFW&NTX   0.17213

1685 FARM SW  345 -  2461 ROYSE    345 2       227.     0.002135    VAL  3 G    SYSTEM    0.42974

1030 MRGN CRK 345 -  1430 GRAHAM   345 1        80.     0.002076    ENCOGN4G    SYSTEM    0.36931

1420 ENCOGEN  345 -  1430 GRAHAM   345 1        80.     0.001900    ENCOGN4G    SYSTEM    0.42856

3391 JEWETT N 345 - 46500 TOMBAL 5 345 1       744.     0.001471    LIM1        HLP       0.20994

1430 GRAHAM   345 -  1873 BENBRK   345 1       399.     0.000915    GRAM 2 G    SYSTEM    0.30891

7042 ZORN  34 345 -  7044 MARION34 345 1       155.     0.000820    GUALUP 2    AustEngy  0.62191

1882 EV WEST  345 -  1906 VENUS S  345 1       280.     0.000706    MELP 2      MINERL W  0.67575

3414 TEMP  SS 345 -  3429 SANDOW   345 1       167.     0.000677    LOSTPN 3    WACO-CTX  0.44183

3123 TRINDAD1 345 -  3133 RICHLND1 345 1       189.     0.000415    CALFRE1G    DFW&NTX   0.30064

1918 SHERRY   345 -  1930 CENTURY3 345 1       818.     0.000345    DEC  1 G    DFW&NTX   0.16406

1870 BENB B T 345 -  1873 BENBRK   345 1       399.     0.000339    GRAM 2 G    SYSTEM    0.24992

2437 FORNEY   345 -  2474 ROYSE T  345 1       189.     0.000260    CALFRE1G    DFW&NTX   0.09959

7044 MARION34 345 -  7045 ZORN  34 345 1       155.     0.000184    GUALUP 2    AustEngy  0.57640

1887 EVER 2BT 345 -  1888 DEC  T   345 1       327.     0.000181    DEC  1 G    SYSTEM    0.32035

1855 ALLIANCE 345 -  1859 EAGLE MT 345 1       379.     0.000177    EGMT 3 G    DFW&NTX   0.24269

2437 FORNEY   345 -  2453 CNVIL    345 1       727.     0.000140    MTNLK 3G    DFW&NTX   0.08787

3413 TEMPSSLT 345 -  3429 SANDOW   345 1       167.     0.000120    LOSTPN 3    WACO-CTX  0.44149

5211 HILL CTY 345 -  7044 MARION34 345 1       155.     0.000111    GUALUP 4    CPS       0.54848

1931 COURTLND 345 -  1933 KENNDLE2 345 1       818.     0.000107    DEC  1 G    DFW&NTX   0.14843

1886 EV EAST  345 -  1907 VENUS N  345 1       280.     0.000105    MELP 3      MINERL W  0.36282

3405 T HOUSE  345 -  3409 LAKE CRK 345 2       578.     0.000087    THSE 1 G    RND ROCK  0.68799

1902 JOHN SS  345 -  1907 VENUS N  345 1       200.     0.000061    TENASKA     SYSTEM    0.36242

1917 SHERRY T 345 -  1931 COURTLND 345 1       818.     0.000051    DEC  1 G    DFW&NTX   0.18340

2428 WATMILLE 345 -  2432 TRICORN  345 1       291.     0.000048    GATEWY4G    SYSTEM    0.22943

44650 SMTHRS 5 345 - 47000 BELAIR 5 345 50      636.     0.000047    WAP6        HLP       0.30981

5400 SPRUCE   345 -  5725 PAWNESW6 345 1       159.     0.000046    LAP #6      CPS       0.44980

3409 LAKE CRK 345 -  3414 TEMP  SS 345 1       578.     0.000044    THSE 1 G    RND ROCK  0.51778

45500 T_H_W_ 5 345 - 45600 ADICKS 5 345 71       85.     0.000041    THW GT51    BPUB      0.30028

3390 JEWETT S 345 - 45500 T_H_W_ 5 345 1       356.     0.000030    NLK  3 G    HLP       0.20516

1906 VENUS S  345 -  3405 T HOUSE  345 1       818.     0.000027    THSE 2 G    DFW&NTX   0.26162

7042 ZORN  34 345 -  9074 LYTTON   345 1       253.     0.000027    HAYSN 3     RND ROCK  0.55832

3405 T HOUSE  345 -  3414 TEMP  SS 345 1       578.     0.000019    THSE 1 G    RND ROCK  0.49990

3380 BIGBRN   345 -  3390 JEWETT S 345 1       327.     0.000016    BBRN 2 G    LIMESTON  0.49812

40255 CHAMBR 5 345 - 40900 KING   5 345 97      210.     0.000011    BTE ST4     LIMESTON  0.53200

5371 SKYLINE  345 -  5400 SPRUCE   345 1       426.     0.000005    JKS1        CPS       0.80675

1422 BOWMAN   345 -  1425 FISHRDSS 345 1       389.     0.000003    OKLAUN1G    SYSTEM    0.54954

2420 C HILL   345 -  2431 DESOTOSW 345 1       213.     0.000003    TRACEN1G    MINERL W  0.24902

5211 HILL CTY 345 -  5371 SKYLINE  345 1       155.     0.000003    GUALUP 1    CPS       0.30424

1029 ODEHV 2T 345 -  1030 MRGN CRK 345 1       180.     0.000002    TIE ST2G    SYSTEM    0.50242

1028 ODEHV 1T 345 -  1030 MRGN CRK 345 1       180.     0.000001    TIE ST2G    SYSTEM    0.47112

3134 RICHLND2 345 -  3380 BIGBRN   345 1       543.     0.000001    BBRN 2 G    DFW&NTX   0.29147

7048 GARFIE34 345 -  9074 LYTTON   345 1       167.     0.000001    LOSTPN 3    RND ROCK  0.35680

The following is a list of the limiting 345 kV circuits in file XXOP0 (N-0 analysis) sorted in decreasing order of the MWH column.  The MWH column is the integral of the circuit flow from the circuit rating to infinity (previously shown as the yellow areas):

BUS#   BUS NAME      BUS#   BUS NAME   ID       MW        MWH      GENERATOR > LOAD AREA    PDF

1907 VENUS N  345 -  1911 WEBB 1   345 1       280.   148.918091    MELP 3      DFW&NTX   0.23146

5915 SO TEX 5 345 - 44000 W_A_P_ 5 345 39     1311.   147.516998    STP1        HLP       0.27671

2436 TRICOR E 345 -  2437 FORNEY   345 1       189.     3.879349    CALFRE1G    DFW&NTX   0.13912

1421 WILLOWCK 345 -  1436 PARKER   345 1       268.     3.533287    WCPP 3 G    SYSTEM    0.69959

5915 SO TEX 5 345 - 42500 DOW345 5 345 18     1311.     3.425071    STP1        HLP       0.23691

1425 FISHRDSS 345 -  6100 OKLAEHV7 345 1       231.     1.411878    OKLAUN1G    W FALLS   0.65948

1911 WEBB 1   345 -  1916 LIG2 T   345 1       280.     0.068846    MELP 3      DFW&NTX   0.22870

1050 ENRONIPP 345 -  6235 ABMULCW7 345 1       400.     0.066162    ENRONIPP    ABILENE   0.59963

3429 SANDOW   345 -  7040 AUSTRO34 345 1       167.     0.049763    LOSTPN 3    WACO-CTX  0.27977

5915 SO TEX 5 345 - 42500 DOW345 5 345 27     1311.     0.011399    STP1        HLP       0.23691

2410 NORWOODT 345 -  2420 C HILL   345 1       280.     0.008009    MELP 2      DFW&NTX   0.16631

5371 SKYLINE  345 -  7044 MARION34 345 1       155.     0.000755    GUALUP 4    CPS       0.43579

967 GIBCRK B 345 - 44500 OBRIEN 5 345 1       462.     0.000714    GIBCRK      HLP       0.31563

3429 SANDOW   345 -  7040 AUSTRO34 345 2       167.     0.000529    LOSTPN 3    WACO-CTX  0.27977

1876 WLFHOL   345 -  1880 ROCKY CK 345 1       304.     0.000372    WLFHOL2G    SYSTEM    0.30760

3123 TRINDAD1 345 -  3133 RICHLND1 345 1       189.     0.000248    CALFRE1G    DFW&NTX   0.30064

42000 P_H_R_ 5 345 - 42500 DOW345 5 345 99      917.     0.000079    DOW2        HLP       0.29258

45500 T_H_W_ 5 345 - 45600 ADICKS 5 345 71       85.     0.000032    THW GT51    BPUB      0.30028

3390 JEWETT S 345 - 45500 T_H_W_ 5 345 1       356.     0.000012    NLK  3 G    HLP       0.20516

1906 VENUS S  345 -  2420 C HILL   345 1       280.     0.000006    MELP 2      DFW&NTX   0.36147

2432 TRICORN  345 -  2433 SGVL SS  345 1       189.     0.000002    CALFRE6G    DFW&NTX   0.13135

The listing below shows contingencies causing additional overloading for three of the circuits listed above.  The severity of each overload below is ranked as the product of MW overload and outage hours of each contingency.  All 345 kV contingencies and 345 kV circuit overloads are given in file XXOP3 (search for overload: to locate the listing):

OVERLOAD:      ----FROM----  -----TO----- ID BASE   N-1  >N-1

1907   1911  VENUS N  345  WEBB 1   345 1  1072  1072  1072

OUTAGES:                                    RATG  RUN#  %OVLD  HOURS  MW*HRS

BASE CASE                                           1   124 3672.00 936804.

2428  46020  WATMILLE 345  LIMEST 5 345 1  1631   124   127    8.06   2324.

2435  46020  WATMLLDB 345  LIMEST 5 345 2  1631   129   127    8.06   2323.

1906   3405  VENUS S  345  T HOUSE  345 1   956    87   126    5.93   1673.

1436   1900  PARKER   345  COM PEAK 345 1  1434    44   129    4.52   1405.

2410   2420  NORWOODT 345  C HILL   345 1  1133   116   154    2.38   1373.

OVERLOAD:      ----FROM----  -----TO----- ID BASE   N-1  >N-1

5915  44000  SO TEX 5 345  W_A_P_ 5 345 39  906  1088  1088

OUTAGES:                                    RATG  RUN#  %OVLD  HOURS  MW*HRS

BASE CASE                                           1   113 3672.00 425688.

5915  42500  SO TEX 5 345  DOW345 5 345 18  906   325   154    1.67    976.

5915  42500  SO TEX 5 345  DOW345 5 345 27  906

42500  44001  DOW345 5 345  WAP_C710 345 99  906   242   113    5.55    766.

42000  42500  P_H_R_ 5 345  DOW345 5 345 99  906   340   132    2.05    709.

42500  44001  DOW345 5 345  WAP_C710 345 99  906

44001  47000  WAP_C710 345  BELAIR 5 345 98  906   249   113    3.33    456.

5915  42500  SO TEX 5 345  DOW345 5 345 18  906   192   106    4.80    291.

OVERLOAD:      ----FROM----  -----TO----- ID BASE   N-1  >N-1

2436   2437  TRICOR E 345  FORNEY   345 1   717   717   717

OUTAGES:                                    RATG  RUN#  %OVLD  HOURS  MW*HRS

2461   3103  ROYSE    345  SHAMBRGR 345 1  1072   137   115    7.41    775.

2432   2433  TRICORN  345  SGVL SS  345 1  1072   125   142    2.16    658.

2427   2436  WATMILLW 345  TRICOR E 345 1   956   120   139    2.31    645.

3100   3103  MARTINLK 345  SHAMBRGR 345 1  1195   139   112    4.66    399.

2396   2428  W LEVP2  345  WATMILLE 345 1  1632   113   121    1.83    275.

Differencing the N-3 and N-0 tables on pages 11 and 12 shows the following 345 kV circuits have probabilistic overloads only when there are other transmission contingencies:

BUS#   BUS NAME      BUS#   BUS NAME   ID       MW        MWH      GENERATOR > LOAD AREA    PDF

1885 EVER 1BT 345 -  1933 KENNDLE2 345 1       818.     0.319578    DEC  1 G    DFW&NTX   0.14292

1436 PARKER   345 -  1859 EAGLE MT 345 1       268.     0.274721    WCPP 3 G    DFW&NTX   0.28738

1873 BENBRK   345 -  1890 DECORDVA 345 1       615.     0.156089    DEC  1 G    W FALLS   0.39665

1430 GRAHAM   345 -  1436 PARKER   345 1       399.     0.034238    GRAM 2 G    SYSTEM    0.40562

1690 VALLEY   345 -  1692 PARIS SS 345 1       341.     0.033445    LPP 6  G    SYSTEM    0.49176

1026 ODES EHV 345 -  1028 ODEHV 1T 345 1       180.     0.019726    TIE ST2G    SYSTEM    0.61476

1917 SHERRY T 345 -  2420 C HILL   345 1       227.     0.014767    DEC  1 G    PALESTIN  0.20326

2427 WATMILLW 345 -  2436 TRICOR E 345 1       510.     0.008053    STRYK 2G    VENUS     0.23582

1025 FS COGEN 345 -  1030 MRGN CRK 345 1        70.     0.006933    CALENG2G    SYSTEM    0.85737

3124 TRINDAD2 345 -  3134 RICHLND2 345 1       189.     0.005379    CALFRE6G    DFW&NTX   0.32182

2436 TRICOR E 345 -  3123 TRINDAD1 345 1       189.     0.005338    CALFRE1G    DFW&NTX   0.20812

1436 PARKER   345 -  1869 BENB A T 345 1       268.     0.004348    WCPP 3 G    SYSTEM    0.42769

1880 ROCKY CK 345 -  1886 EV EAST  345 1       304.     0.003722    WLFHOL2G    SYSTEM    0.29079

1695 MOSES    345 -  1697 SULSP SS 345 1       227.     0.003654    MOSES2 G    SYSTEM    0.38880

1430 GRAHAM   345 -  6230 ABMULCE7 345 1       615.     0.002795    OKLAUN1G    W FALLS   0.38452

44000 W_A_P_ 5 345 - 44650 SMTHRS 5 345 50      636.     0.002491    WAP6        HLP       0.31607

1886 EV EAST  345 -  1932 KENNDLE1 345 1       818.     0.002259    DEC  1 G    DFW&NTX   0.17213

1685 FARM SW  345 -  2461 ROYSE    345 2       227.     0.002135    VAL  3 G    SYSTEM    0.42974

1030 MRGN CRK 345 -  1430 GRAHAM   345 1        80.     0.002076    ENCOGN4G    SYSTEM    0.36931

1420 ENCOGEN  345 -  1430 GRAHAM   345 1        80.     0.001900    ENCOGN4G    SYSTEM    0.42856

3391 JEWETT N 345 - 46500 TOMBAL 5 345 1       744.     0.001471    LIM1        HLP       0.20994

1430 GRAHAM   345 -  1873 BENBRK   345 1       399.     0.000915    GRAM 2 G    SYSTEM    0.30891

7042 ZORN  34 345 -  7044 MARION34 345 1       155.     0.000820    GUALUP 2    AustEngy  0.62191

1882 EV WEST  345 -  1906 VENUS S  345 1       280.     0.000706    MELP 2      MINERL W  0.67575

3414 TEMP  SS 345 -  3429 SANDOW   345 1       167.     0.000677    LOSTPN 3    WACO-CTX  0.44183

1918 SHERRY   345 -  1930 CENTURY3 345 1       818.     0.000345    DEC  1 G    DFW&NTX   0.16406

1870 BENB B T 345 -  1873 BENBRK   345 1       399.     0.000339    GRAM 2 G    SYSTEM    0.24992

2437 FORNEY   345 -  2474 ROYSE T  345 1       189.     0.000260    CALFRE1G    DFW&NTX   0.09959

7044 MARION34 345 -  7045 ZORN  34 345 1       155.     0.000184    GUALUP 2    AustEngy  0.57640

1887 EVER 2BT 345 -  1888 DEC  T   345 1       327.     0.000181    DEC  1 G    SYSTEM    0.32035

1855 ALLIANCE 345 -  1859 EAGLE MT 345 1       379.     0.000177    EGMT 3 G    DFW&NTX   0.24269

2437 FORNEY   345 -  2453 CNVIL    345 1       727.     0.000140    MTNLK 3G    DFW&NTX   0.08787

3413 TEMPSSLT 345 -  3429 SANDOW   345 1       167.     0.000120    LOSTPN 3    WACO-CTX  0.44149

5211 HILL CTY 345 -  7044 MARION34 345 1       155.     0.000111    GUALUP 4    CPS       0.54848

1931 COURTLND 345 -  1933 KENNDLE2 345 1       818.     0.000107    DEC  1 G    DFW&NTX   0.14843

1886 EV EAST  345 -  1907 VENUS N  345 1       280.     0.000105    MELP 3      MINERL W  0.36282

3405 T HOUSE  345 -  3409 LAKE CRK 345 2       578.     0.000087    THSE 1 G    RND ROCK  0.68799

1902 JOHN SS  345 -  1907 VENUS N  345 1       200.     0.000061    TENASKA     SYSTEM    0.36242

1917 SHERRY T 345 -  1931 COURTLND 345 1       818.     0.000051    DEC  1 G    DFW&NTX   0.18340

2428 WATMILLE 345 -  2432 TRICORN  345 1       291.     0.000048    GATEWY4G    SYSTEM    0.22943

44650 SMTHRS 5 345 - 47000 BELAIR 5 345 50      636.     0.000047    WAP6        HLP       0.30981

5400 SPRUCE   345 -  5725 PAWNESW6 345 1       159.     0.000046    LAP #6      CPS       0.44980

3409 LAKE CRK 345 -  3414 TEMP  SS 345 1       578.     0.000044    THSE 1 G    RND ROCK  0.51778

1906 VENUS S  345 -  3405 T HOUSE  345 1       818.     0.000027    THSE 2 G    DFW&NTX   0.26162

7042 ZORN  34 345 -  9074 LYTTON   345 1       253.     0.000027    HAYSN 3     RND ROCK  0.55832

3405 T HOUSE  345 -  3414 TEMP  SS 345 1       578.     0.000019    THSE 1 G    RND ROCK  0.49990

3380 BIGBRN   345 -  3390 JEWETT S 345 1       327.     0.000016    BBRN 2 G    LIMESTON  0.49812

40255 CHAMBR 5 345 - 40900 KING   5 345 97      210.     0.000011    BTE ST4     LIMESTON  0.53200

5371 SKYLINE  345 -  5400 SPRUCE   345 1       426.     0.000005    JKS1        CPS       0.80675

1422 BOWMAN   345 -  1425 FISHRDSS 345 1       389.     0.000003    OKLAUN1G    SYSTEM    0.54954

2420 C HILL   345 -  2431 DESOTOSW 345 1       213.     0.000003    TRACEN1G    MINERL W  0.24902

5211 HILL CTY 345 -  5371 SKYLINE  345 1       155.     0.000003    GUALUP 1    CPS       0.30424

1029 ODEHV 2T 345 -  1030 MRGN CRK 345 1       180.     0.000002    TIE ST2G    SYSTEM    0.50242

1028 ODEHV 1T 345 -  1030 MRGN CRK 345 1       180.     0.000001    TIE ST2G    SYSTEM    0.47112

3134 RICHLND2 345 -  3380 BIGBRN   345 1       543.     0.000001    BBRN 2 G    DFW&NTX   0.29147

7048 GARFIE34 345 -  9074 LYTTON   345 1       167.     0.000001    LOSTPN 3    RND ROCK  0.35680

A complete listing of the contingencies and their severities are shown in file XXOP3 after each occurrence of “overload:”.  Severities are ranked by the products of MW of circuit overload times the expected outage hours of each contingency.  No generator outages are taken in this listing.

Studies were also performed in which 138 kV circuits are included in the study.  The overall transmission LOLE for these studies is graphed on pages 7 and 9.  A list of 138 kV limiting circuits is given below in the N-0 base case from file OP0.

BUS#   BUS NAME      BUS#   BUS NAME   ID       MW        MWH      GENERATOR > LOAD AREA    PDF

1951 HANDLEYD 138 -  2109 WHITE 1T 138 1       430.   261.529755    HAND 4 G    SYSTEM    0.15738

42500 DOW345 5 345 - 42510 DOW138 8 138 A1      986.   206.749664    DOW1        HLP       0.15447

1027 ODES EHV 138 -  1128 LIQD AIR 138 1       180.   179.999451    TIE ST2G    MIDLAND   0.09911

1918 SHERRY   345 -  1920 SHERRY B 138 1       280.   179.962540    MELP 2      DFW       0.07834

6022 ENR_STP4 138 -  6582 MVIEWTP2 138 1        80.    15.024394    ENR_SP      SYSTEM    0.57620

1875 BENBRK B 138 -  2174 HORNE 13 138 1       399.    14.846711    GRAM 2 G    SYSTEM    0.03718

47610 CE_SIDE8 138 - 47750 UNIVER 8 138 91      140.    11.187838    AES1        SYSTEM    0.29541

9187 DECKER   138 -  9271 SPRINKLE 138 1       306.     6.945491    DECKR G2    LCRA-N    0.27586

2453 CNVIL    345 -  2454 CNVIL    138 1       150.     5.326462    OLINGR3     DFW       0.10316

1146 YORK IPP 138 -  1149 DOLRHIDE 138 1        80.     3.805273    YORK IPP    SYSTEM    0.37374

42515 DOW_A_   138 - 42500 DOW345 5 345 A3      356.     3.562289    NLK  3 G    SYSTEM    0.02916

8314 LAPALM 4 138 -  8333 L.FRES 4 138 1       101.     3.191142    LAP #6      DC-MEX    0.39238

7202 HICROS13 138 -  7356 MARSFO13 138 1        45.     1.710330    SANDH G3    LCRA-N    0.11038

1919 SHERRY A 138 -  1920 SHERRY B 138 1       430.     1.656377    HAND 4 G    SYSTEM    0.07012

1883 EVERMN A 138 -  2224 OAK H 1T 138 1        89.     0.949735    DECT D G    SYSTEM    0.04219

6579 FTLCSTR2 138 -  6582 MVIEWTP2 138 1        80.     0.516326    ENR_SP      SYSTEM    0.28370

1339 ESKOTA   138 -  6260 ABSOUTH4 138 1       114.     0.497584    TRENTIPP    ABILENE   0.39920

2434 SGVL SS  138 -  2779 LAWSON   138 1       240.     0.141622    TDAD 6 G    DAL SUBS  0.08527

2164 HEMPHILL 138 -  2173 MIST 34  138 1       399.     0.079427    GRAM 2 G    SYSTEM    0.02565

1099 SWPORT T 138 -  1102 JUDKINS  138 1       167.     0.037361    PB   6 G    SYSTEM    0.15315

47600 E_SIDEB8 138 - 47610 CE_SIDE8 138 91      140.     0.030352    AES1        SYSTEM    0.29475

1886 EV EAST  345 -  1884 EVERMN B 138 1       280.     0.020674    MELP 2      SYSTEM    0.04217

7150 KENDAL13 138 -  7046 KENDAL34 345 1        52.     0.016537    HAYSN 1     WTU/LCRA  0.18061

6014 SWMTP2   138 -  6536 BIGLAK24 138 1        75.     0.016360    SWMESA      SYSTEM    0.31374

2054 IRVING   138 -  2408 NORWOD 1 138 1       531.     0.012404    MTCK 8 G    SYSTEM    0.05040

5005 AUSTIN   138 -  5435 TUTTLE   138 1       100.     0.011174    WBT3        SYSTEM    0.22398

1197 CRANE    138 -  1199 ARCO C T 138 1        80.     0.001628    KM_NWP      MIDLAND   0.42040

47515 AUSTIN 8 138 - 47730 POLK   8 138 90      140.     0.001557    AES1        SYSTEM    0.21372

42210 BRZPRT 8 138 - 43360 VLASCO 8 138 02      986.     0.001472    DOW1        SYSTEM    0.04890

1010 PERMIANB 138 -  1019 MOSS     138 1       139.     0.000149    PB   6 G    SYSTEM    0.17775

33 WATSONCP 138 -  3392 JEWETT   138 1       240.     0.000088    TDAD 6 G    BRYAN     0.08860

2173 MIST 34  138 -  2174 HORNE 13 138 1       399.     0.000063    GRAM 2 G    SYSTEM    0.02910

2184 WDGWD NT 138 -  2196 PRIMRSE1 138 1       291.     0.000042    WLFHOL2G    SYSTEM    0.04208

501 HILTOP   138 -   512 NWTHRFRD 138 1       126.     0.000038    MILLER3     SYSTEM    0.19598

5200 HELOTES  138 -  7151 CICO  13 138 1        52.     0.000022    LCP4        WTU/LCRA  0.17225

6309 PUTNAM 4 138 -  6773 PCANBYU4 138 1        25.     0.000022    PHANTM2G    TNP/VROG  0.12840

1027 ODES EHV 138 -  1199 ARCO C T 138 1        80.     0.000017    KM_NWP      SYSTEM    0.39574

47515 AUSTIN 8 138 - 47660 GARROT 8 138 90      140.     0.000011    AES1        SYSTEM    0.21326

42810 HOFMAN   138 - 42880 LKJACK 8 138 02       80.     0.000006    BASF1       SYSTEM    0.26981

7328 AUSTRO13 138 -  9187 DECKER   138 2       340.     0.000002    GIDEONG3    AustEngy  0.18272

1882 EV WEST  345 -  1883 EVERMN A 138 1       280.     0.000001    MELP 2      SYSTEM    0.04686

Loss of Load Methodology (unserved energy by load area in file OP3):

LOLE transmission statistics are assigned to the load areas in which load is shed.  In the PLF model, a transmission circuit that is overloaded is associated with a load area and the generators with the highest PDFs.  The load area will typically be physically in the vicinity of the receiving end of power flowing over the overloaded circuit to the receiving area.  The generator will be on the other side of the overloaded circuit.  When the power is simultaneously reduced on the generator and the load, the circuit overload is removed with the least amount of MW reduction.

The graph below shows the transmission EUE for N-3 level of contingencies for the individual load areas with the highest unserved energies due to transmission constraints.

An alternate way of reviewing the amount of load shedding going on in each load area is shown below.  The table below lists the unserved MWh energy during a period of one hour when the ERCOT load is 62956 MW.  This information comes from file OP3 in which both 138 kV and 345 kV circuits are outaged.

EUE-MWh  Area    Name       EUE-MWh  Area    Name       EUE-MWh  Area    Name       EUE-MWh  Area    Name

0.00000   200  EHVDC        0.00017   450  NORTHERN     0.00165   124  COMANCHE     0.56984   507  LCRA-N

0.00000   319  HLP/LCAP     0.00018   655  MVEC/W       0.00269   140  GAINESVL     0.58385     4  GARLAND

0.00001   659  CPL/MEC      0.00021   640  NORTH LI     0.00341   144  TYLER        0.73061   131  DFW

0.00002   235  TNP/HC-F     0.00022   142  SULPHR S     0.00343   709  AustEngy     0.84277   506  LCRA-W

0.00004   220  TNP/CLIF     0.00025   438  WESTERN      0.00359   222  TNP/VROG     0.94200   393  WTU/LCRA

0.00004   221  TNP/WLSP     0.00025   474  SAN ANG      0.00396   350  CPS          0.95999     3  DENTON

0.00004   310  STP          0.00025   801  DC-MEX       0.00428   151  TEMPLE       1.13138     2  BRYAN

0.00005   225  TNP/KTRC     0.00026   141  PARIS        0.00511   143  WILLS PT     1.15951   125  MINERL W

0.00007   154  HILLSBOR     0.00026   149  LIMESTON     0.00679   134  VENUS        1.28391    11  BEPC

0.00007   654  MVEC/E       0.00035   610  E VALLEY     0.00735   145  ATHENS       1.53806   152  KILLEEN

0.00008   870  MEC          0.00040   401  WRYBRN       0.00966   227  TNP/CLMX     2.23949   800  BPUB

0.00009   175  SESCO-E      0.00053   645  CENT LI      0.01706   301  HLP          2.31291   890  STEC

0.00009   400  WTUTEXLA     0.00054   620  N REGION     0.02668   176  SESCO-W      4.63386   135  DAL SUBS

0.00014     6  TMPA/GVL     0.00077   630  W REGION     0.05069   432  ABILENE     22.16757   504  LCRA-E

0.00014   148  CORSICAN     0.00084   615  W VALLEY     0.05082   146  LUFKIN      57.40374   161  MIDLAND

0.00016   440  CENTRAL      0.00104   625  C REGION     0.06742   153  WACO        99.17506        total

0.00016   470  SOUTHERN     0.00108   147  PALESTIN     0.16699   512  LCRA-S      (see line 108025 in OP3)

0.00017   121  EASTLAND     0.00160   150  RND ROCK     0.23315   120  W FALLS

Loss of Load Methodology (cont.):

Every generator not forced out of service is run at maximum output.  If there are no transmission constraints (i.e. single area analysis in Phase II), the load that can be served is the sum of all the installed generation that is available at any time.  Any load above what can be generated is loss of load.  Without transmission constraints, as in the single area analysis, or in an extremely reliable transmission system, the load at each substation has the same reliability as the generation supply for the entire system.  When transmission constraints are introduced, they will be site specific, dependent on the nature of the transmission constraints.  If there are transmission constraints, less power can be delivered to the load.

PLF has the ability to interrupt contracted transactions.  However, no bilateral transaction data was entered into the data for this study.  Such data can significantly alter which areas receive the load shedding.

For any specific limiting circuit, if the load PDF is less than 3%, then load is shed uniformly throughout ERCOT as the offending generator is reduced in power.  If power is sent to the system and the total PDF is well above 3%, then that limiting circuit is very near the offending generator and reducing the generator output reduces the circuit overload.  If a generator is quite remote from a limiting circuit, then the circuit overload is probably due to serving load.  If the PDF for such a circuit is low, then the load shedding areas are not well defined in the data, i.e. the area being load shed is not optimum and is probably not the set of bus loads the operators would have chosen.  In this instance the area definition data needs to be corrected.

The PLF program minimizes the amount of load being shed by selecting generators and loads that have the highest distribution factors for removing the overload condition.  How the load shedding areas are defined affects the load shedding amounts and how they are assigned.

Creating Load Shedding Areas:

Load shed areas are created from zones in the 2003 load flow data.  The original 2003 case had only one major area called ERCOT.  Although this could have been used, it would have given incorrect answers since every transmission constraint would have caused load shedding in the entire ERCOT system.

New load shedding areas are created by copying the zone data onto the area data within the PSS/E raw data file.  These areas are numerous and small in MW load.  There are many instances in which the MW of load shedding exceeds the load within the area receiving the load shedding.  To overcome this problem, areas (zones) are combined together based on which zones can be used to unload an overloaded  circuit.  The PDFs of load shedding zones are identified for the top overloaded circuits.  These zones are lumped together to create new load shedding areas.  This results in clustering of zones within North Texas and within the Houston area and clustering together the zones within LCRA, AEP, and AEN to make more logical load shedding areas.  Some of the smaller load areas and zones are left unchanged (when no transmission constraints cause undue load shedding).  The load shedding areas are different for the 138 kV and 345 kV studies.

The following areas are defined in the 345 kV study (in files XXOP3 and XXOP).

GENERATION      ---LOAD---       ---LOSS---   INTERCHANGE  DIFF

A#   AREA      MW     MVAR     MW     MVAR      MW    MVAR     MW   MVAR   MW

-- --------  ------  ------  ------  ------   ------ ------  ----- -----  ----

2 BRYAN        243      88     408      75      5.1     47   -170   -34  0.00

11 BEPC        1709    1238    2921     906     84.1    349  -1296   -16 -0.01

120 W FALLS        0       0     615     146     34.1     90   -649  -236  0.00

121 EASTLAND     640     331     181      32     51.7    158    407   140  0.00

124 COMANCHE       0       0     242      63     13.8      0   -256   -64  0.00

125 MINERL W     700     657     291      69     18.7    104    390   484  0.00

131 DFW&NTX    16520    8589   23566    6990    755.3   3439  -7801 -1840 -0.03

134 VENUS       5972    2852    1286     429    127.7   1264   4559  1158  0.02

147 PALESTIN     691     244     227      68     24.0     39    440   135  0.00

149 LIMESTON     308      56     327      72      3.5    -93    -22    77  0.00

150 RND ROCK     897     350    1435     494     17.3    -29   -555  -114  0.00

151 TEMPLE         0       0     411     113     12.9     21   -423  -135  0.00

153 WACO-CTX    1716     712    1412     394     37.7    116    267   202  0.00

154 HILLSBOR       0       0      98      26      8.1    -16   -106   -10  0.00

161 MIDLAND     4725    1688    2169     664    214.9   1014   2341     9  0.00

176 SESCO-W        0       0     111      35      1.5    -14   -112   -20  0.00

200 EHVDC        700       0       0       0      3.6     37    696   -37  0.00

221 TNP/WLSP       0       0      59       8      1.0    -28    -60    20  0.00

222 TNP/VROG       0       0      25       3      0.2      0    -26    -3  0.00

301 HLP        23426    8811   25161    5476    326.1   3720  -2061  -385  0.00

310 STP         2622     664       0       0     59.1    759   2563   -95  0.00

319 HLP/LCAP       0       0       0       0      2.6  -1047     -3  1047  0.00

350 CPS         4208    1219    5239    1529     55.2   -397  -1086    87  0.00

393 WTU/LCRA       0       0      52      12      0.9      1    -53   -13  0.00

394 NHVDC        220       0       0       0      0.0    -61    220    61  0.00

432 ABILENE       18      62     426     128     26.5      0   -434   -66  0.00

438 WESTERN      953     280     269      99     77.1    254    607   -74 -0.01

440 CENTRAL      362     162     210      61     15.8     48    136    53  0.00

450 NORTHERN     971     170     193      68     33.9     78    744    24  0.00

470 SOUTHERN      85      72     182      64     38.0    121   -135  -113  0.00

474 SAN ANG      123     171     307      82     27.7    153   -212   -64  0.00

504 LCRA-E      3239    1173     698     174     50.3    397   2490   601  0.00

506 LCRA-W         6       0    1230     329     27.7   -114  -1252  -214  0.00

507 LCRA-N       703     345    1091     303     31.6   -115   -419   157  0.00

512 LCRA-S      2980     599     674     144     34.8    531   2271   -76  0.00

610 E VALLEY     261     279     451      78     23.2    184   -213    15  0.00

615 W VALLEY    2005     439    1106     284     29.9    265    869  -109  0.00

620 N REGION    1377     287     676     172     52.3    162    648   -46  0.00

625 C REGION    2321     575    1342     332     51.7    121    927   121  0.00

630 W REGION     188     412     979     179     63.2    127   -854   106  0.02

640 NORTH LI       0      30     288      53      1.4      6   -290   -29  0.00

645 CENT LI      530     182     708     229      5.0     83   -183  -130  0.00

651 CR COGEN     450      82       0       0      0.0     40    450    41  0.00

654 MVEC/E         0       0      85      24      8.7     17    -94   -42  0.00

655 MVEC/W         0       0     242      71      6.0     17   -248   -88  0.00

659 CPL/MEC        0       0      14       2      1.4      3    -15    -6  0.00

709 AustEngy    1758     827    3210    1122     83.9    286  -1536  -581  0.00

800 BPUB          80     134     597      42      1.5     25   -519    66  0.00

870 MEC           70      30     110      34      7.8      8    -48   -13  0.00

890 STEC         539     187     414     124     22.3      9    102    53  0.00

TOTALS     84316   34013   81735   21819   2580.7  12193

The generation within each area is the generation physically located within the area.  There is no ownership information in the above table.  The load flow bus loads have been uniformly scaled throughout ERCOT to match total generation less total losses.  Area loads are the sum of bus loads within areas.  There is no area interchange.  Area interchange is calculated after the fact during the load flow solution process.  All generation is at maximum output with no Var limits on generators, i.e. the effects of voltage variations, including voltage collapse, are not considered.

The following areas are defined in the 138 and 345 kV study (in files OP3 and OP0).

GENERATION      ---LOAD---       ---LOSS---   INTERCHANGE  DIFF

A#   AREA      MW     MVAR     MW     MVAR      MW    MVAR     MW   MVAR   MW

-- --------  ------  ------  ------  ------   ------ ------  ----- -----  ----

2 BRYAN        243      88     408      75      5.1     47   -170   -34  0.00

3 DENTON       178     118     363      16      2.5     31   -187    71  0.00

4 GARLAND      505     308     641     111     13.9    183   -150    13  0.00

6 TMPA/GVL     549     275     173       5     15.0    255    361    14  0.00

11 BEPC        1709    1238    2921     906     84.1    349  -1296   -16 -0.01

120 W FALLS        0       0     615     146     34.1     90   -649  -236  0.00

121 EASTLAND     640     331     181      32     51.7    158    407   140  0.00

124 COMANCHE       0       0     242      63     13.8      0   -256   -64  0.00

125 MINERL W     700     657     291      69     18.7    104    390   484  0.00

131 DFW         4711    3420   12915    3872    340.5   1735  -8544 -2188 -0.03

134 VENUS       5972    2852    1286     429    127.7   1264   4559  1158  0.02

135 DAL SUBS     475     830    5666    1841     96.0   -881  -5287  -129 -0.03

140 GAINESVL      80      43     509     144     10.8     -5   -439   -95  0.00

141 PARIS       2573    1025     287      76     64.0    662   2222   286  0.01

142 SULPHR S    1812     921     212      61     86.2    573   1514   287  0.01

143 WILLS PT       0       0      87      23      2.7      0    -89   -22  0.00

144 TYLER       3135     997     717     211     49.9    671   2368   114  0.01

145 ATHENS      1374     355     168      47     49.9    285   1156    22  0.01

146 LUFKIN        42       0     714     262      9.4    -95   -681  -166  0.00

147 PALESTIN     691     244     227      68     24.0     39    440   135  0.00

148 CORSICAN    1086     291     174      46     10.5     26    902   218  0.00

149 LIMESTON     308      56     327      72      3.5    -93    -22    77  0.00

150 RND ROCK     897     350    1435     494     17.3    -29   -555  -114  0.00

151 TEMPLE         0       0     411     113     12.9     21   -423  -135  0.00

152 KILLEEN        0       0     550     155      8.4    -26   -558  -128  0.00

153 WACO        1716     712     809     230     24.6    152    882   329  0.00

154 HILLSBOR       0       0      98      26      8.1    -16   -106   -10  0.00

161 MIDLAND     4725    1688    2169     664    214.9   1014   2341     9  0.00

175 SESCO-E        0       0     125      35      0.7      0   -125   -35  0.00

176 SESCO-W        0       0     111      35      1.5    -14   -112   -20  0.00

200 EHVDC        700       0       0       0      3.6     37    696   -37  0.00

220 TNP/CLIF       0       0      52       8      4.7     -9    -57     1  0.00

221 TNP/WLSP       0       0      59       8      1.0    -28    -60    20  0.00

222 TNP/VROG       0       0      25       3      0.2      0    -26    -3  0.00

225 TNP/KTRC       0       0      78      16      0.7      0    -79   -16  0.00

227 TNP/CLMX       0       0      29       6      0.3      0    -29    -6  0.00

235 TNP/HC-F       0       0      35      10      0.0      0    -35   -10  0.00

301 HLP        23426    8811   25161    5476    326.1   3720  -2061  -385  0.00

310 STP         2622     664       0       0     59.1    759   2563   -95  0.00

319 HLP/LCAP       0       0       0       0      2.6  -1047     -3  1047  0.00

350 CPS         4208    1219    5239    1529     55.2   -397  -1086    87  0.00

393 WTU/LCRA       0       0      52      12      0.9      1    -53   -13  0.00

394 NHVDC        220       0       0       0      0.0    -61    220    61  0.00

400 WTUTEXLA       0       0     131      28      0.1     -3   -131   -25  0.00

401 WRYBRN         0       0     544     171      2.1     -1   -546  -170  0.00

432 ABILENE       18      62     426     128     26.5      0   -434   -66  0.00

438 WESTERN      953     280     269      99     77.1    254    607   -74 -0.01

440 CENTRAL      362     162     210      61     15.8     48    136    53  0.00

450 NORTHERN     971     170     193      68     33.9     78    744    24  0.00

470 SOUTHERN      85      72     182      64     38.0    121   -135  -113  0.00

474 SAN ANG      123     171     307      82     27.7    153   -212   -64  0.00

504 LCRA-E      3239    1173     698     174     50.3    397   2490   601  0.00

506 LCRA-W         6       0    1230     329     27.7   -114  -1252  -214  0.00

507 LCRA-N       703     345    1091     303     31.6   -115   -419   157  0.00

512 LCRA-S      2980     599     674     144     34.8    531   2271   -76  0.00

610 E VALLEY     261     279     451      78     23.2    184   -213    15  0.00

615 W VALLEY    2005     439    1106     284     29.9    265    869  -109  0.00

620 N REGION    1377     287     676     172     52.3    162    648   -46  0.00

625 C REGION    2321     575    1342     332     51.7    121    927   121  0.00

630 W REGION     188     412     979     179     63.2    127   -854   106  0.02

640 NORTH LI       0      30     288      53      1.4      6   -290   -29  0.00

645 CENT LI      530     182     708     229      5.0     83   -183  -130  0.00

651 CR COGEN     450      82       0       0      0.0     40    450    41  0.00

654 MVEC/E         0       0      85      24      8.7     17    -94   -42  0.00

655 MVEC/W         0       0     242      71      6.0     17   -248   -88  0.00

659 CPL/MEC        0       0      14       2      1.4      3    -15    -6  0.00

709 AustEngy    1758     827    3210    1122     83.9    286  -1536  -581  0.00

800 BPUB          80      84     297      42      1.5     25   -218    16  0.00

801 DC-MEX         0      49     301       0      0.0      0   -301    49  0.00

870 MEC           70      30     110      34      7.8      8    -48   -13  0.00

890 STEC         539     187     414     124     22.3      9    102    53  0.00

TOTALS     84316   34013   81735   21819   2580.7  12194

The following areas are defined in the 138 and 345 kV study with 50% of the new generation scheduled from 2000 – 2003 (in files OP3-50 and OP0-50).

GENERATION      ---LOAD---       ---LOSS---   INTERCHANGE  DIFF

A#   AREA      MW     MVAR     MW     MVAR      MW    MVAR     MW   MVAR   MW

-- --------  ------  ------  ------  ------   ------ ------  ----- -----  ----

2 BRYAN        243      65     372      68      4.1     40   -133   -43  0.00

3 DENTON       178      58     331      14      1.6     22   -154    21  0.00

4 GARLAND      468     203     585     101     10.6    145   -128   -43  0.00

6 TMPA/GVL     549     238     158       5     10.9    199    380    33  0.00

11 BEPC        1584    1008    2662     825     66.8    228  -1145   -45  0.01

120 W FALLS        0       0     560     133     23.0     22   -583  -155  0.00

121 EASTLAND     640     161     165      29     29.2    -52    446   184  0.00

124 COMANCHE       0       0     220      58      8.3    -36   -229   -21  0.00

125 MINERL W     350     391     265      63     12.4     23     72   304  0.00

131 DFW         4709    2003   11771    3530    231.4     59  -7294 -1586  0.01

134 VENUS       5294    1864    1172     391     89.0    669   4033   803 -0.01

135 DAL SUBS     316     403    5164    1678     70.7  -1450  -4920   174  0.01

140 GAINESVL      80      28     464     131      9.0    -24   -393   -78  0.00

141 PARIS       2296     684     262      69     48.4    460   1985   153  0.00

142 SULPHR S    1812     675     193      55     74.4    431   1544   188  0.00

143 WILLS PT       0       0      79      21      2.1     -3    -81   -17  0.00

144 TYLER       2658     639     653     192     37.7    381   1967    64  0.00

145 ATHENS       807     148     153      43     34.0     44    620    60  0.00

146 LUFKIN        42       0     651     238      6.9   -136   -615  -102  0.00

147 PALESTIN     691     159     206      62     20.0      0    465    97  0.00

148 CORSICAN    1086     179     158      42      7.8     -3    920   139  0.00

149 LIMESTON     308      31     298      65      3.4    -99      7    65  0.00

150 RND ROCK     897     259    1308     450     14.3    -55   -425  -135  0.00

151 TEMPLE         0       0     374     103      9.5    -19   -384   -84  0.00

152 KILLEEN        0       0     501     141      6.5    -61   -508   -79  0.00

153 WACO        1716     527     738     210     21.6     97    957   219  0.00

154 HILLSBOR       0       0      89      24      5.7    -28    -95     4  0.00

161 MIDLAND     3771     755    1977     605    122.3    236   1671   -87  0.00

175 SESCO-E        0       0     114      31      0.6      0   -114   -32  0.00

176 SESCO-W        0       0     101      32      1.3    -16   -102   -15  0.00

200 EHVDC        700       0       0       0      3.5     35    696   -35  0.00

220 TNP/CLIF       0       0      48       7      3.6    -17    -51     9  0.00

221 TNP/WLSP       0       0      53       7      0.8    -30    -54    23  0.00

222 TNP/VROG       0       0      23       3      0.1      0    -23    -2  0.00

225 TNP/KTRC       0       0      71      15      0.5      0    -71   -14  0.00

227 TNP/CLMX       0       0      26       5      0.2      0    -27    -6  0.00

235 TNP/HC-F       0       0      32       9      0.0      0    -32    -9  0.00

301 HLP        22169    6912   22933    4991    267.0   2608  -1031  -687  0.00

310 STP         2622     484       0       0     39.6    562   2582   -78  0.00

319 HLP/LCAP       0       0       0       0      2.0  -1093     -2  1093  0.00

350 CPS         4208     936    4775    1394     56.7   -470   -624    13  0.00

393 WTU/LCRA       0       0      47      10      0.6      0    -48   -11  0.00

394 NHVDC        220       0       0       0      0.0    -63    220    63  0.00

400 WTUTEXLA       0       0     119      26      0.1     -3   -119   -22  0.00

401 WRYBRN         0       0     496     156      1.6     -3   -498  -153  0.00

432 ABILENE       18      25     388     116     13.8    -35   -384   -56  0.00

438 WESTERN      588      92     245      91     32.2     57    310   -56  0.00

440 CENTRAL      362     123     192      56     10.0     34    160    32  0.00

450 NORTHERN     971      27     176      62     28.3     35    766   -69  0.00

470 SOUTHERN      85      56     165      58     18.6     25    -99   -27  0.00

474 SAN ANG      123     110     280      74     12.0    -10   -169    46  0.00

504 LCRA-E      2739     826     636     159     35.0    247   2067   419  0.00

506 LCRA-W         6       0    1121     300     19.3   -198  -1134  -101  0.00

507 LCRA-N       703     230     994     276     23.7   -190   -315   144  0.00

512 LCRA-S      1498     197     615     131     19.8     34    864    31  0.00

610 E VALLEY     261     205     411      71     18.7    151   -169   -17  0.00

615 W VALLEY    1630     364    1008     258     22.2    174    600   -68  0.00

620 N REGION    1377     220     616     157     43.3    118    717   -55  0.00

625 C REGION    2321     502    1224     302     46.6     77   1051   122  0.00

630 W REGION     188     327     892     163     38.9     42   -743   121  0.01

640 NORTH LI       0      11     263      48      1.1      3   -264   -40  0.00

645 CENT LI      265     145     645     209      4.0     34   -384   -97  0.00

651 CR COGEN     450      55       0       0      0.0     40    450    15  0.00

654 MVEC/E         0       0      77      22      6.8     11    -84   -34  0.00

655 MVEC/W         0       0     220      64      4.0      8   -224   -72  0.00

659 CPL/MEC        0       0      13       2      1.0      1    -14    -4  0.00

709 AustEngy    1668     613    2926    1022     70.0     65  -1328  -473  0.00

800 BPUB          80      78     271      38      1.2     20   -192    18  0.00

801 DC-MEX         0      31     274       0      0.0      0   -274    31  0.00

870 MEC           70      23     100      31      6.5      3    -37   -10  0.00

890 STEC         539     132     377     113     17.8    -16    143    34  0.00

TOTALS     76353   23220   74499   19888   1854.5   3332

Transmission FOR Methodology:

In the 138 and 345 kV transmission analysis, one thousand circuits and autotransformers are selected out of a total of 3398.  In the 345 kV study, 257 circuits are selected out of 270.   Generator step-up transformers are excluded as well as all circuits and transformers connected to buses less than either 100 kV or 300 kV respectively.  The selected circuits are the most heavily overloaded circuits due to single circuit outages in the base case (non probabilistic).  Circuit outages causing other heavy circuit overloads are also selected.  The selected (retained) set of circuits includes both monitored and outaged circuits.  Single circuit outages causing system separation (islanding) are skipped from further analysis.  LOLE due to islanding is not calculated.

Multiple circuits to be outaged together are given in file COMM2.  PLF calculates the probability of all combinations of single and multiple circuit outages through triple circuit outages (N-3).  If an outage probability is too low, the contingency will be skipped from further analysis.  In this study, the cutoff probability is .03 hours out of a total study period hours of 3672, which is .03/3672 = 8.17e-6.  File COMM2 allows circuits on common structures to have a higher probability of outage than if the circuits were independently randomly outaged.

PLF uses the generic transmission FOR = .0004 + .00002*L where L is the circuit length in miles.  A circuit with a length of 100 miles would have an FOR of .0024 which is equivalent to about 8.8 hours/year for the summer study period used in this study (.0024*3672 hr).  A circuit of 0 length has an FOR=.0004 which easily passes the 8.17e-6 cutoff test.  However, two circuits randomly outaged will only pass this test if they have a length longer than 8.17e-6=(.0004+.00002*L) 2, or rather L>122 miles.  They need not be on the same right of way.  However, they must also pass another test that says they must have an electrical coupling of at least 3%, i.e. the interrupted current in the outaged circuit causes at least 3% of that amount of current in the circuit being tested for overload.  The common circuit FOR in COMM2 overcomes the probability test limitation by allowing shorter circuits to pass the probability minimum cutoff of 8.17e-6, for circuits down to a length of 8.17e-6 ≈ .00001*L, or rather L>0.8 miles.  Usually circuits in COMM2 will be electrically close enough to pass the 3% electrical coupling test.  If not, then the common circuits will not be outaged even if they are listed in COMM2.

For autotransformers, an FOR of .02 (no generator step-ups are outaged) is used.  This is equivalent to a 6 month outage time every 25 years or a 1 year outage time every 12 years.  Two autotransformers outaged simultaneously have an FOR=(.02)2 = .0004, which easily passes the 8.17e-6 probability cutoff test.  However, three autotransformers have a probability of being randomly simultaneously out of service of (.02)3 = 8e-6, which barely fails the test and will not be run.  I found through extensive testing that  allowing all combinations of three autotransformers to be outaged doubles the number of cases to be studied, doubles the computer runtime, and creates many problems in the system.  However, the very low probability of these events, even when taken all together, amounted to only a small increase in the overall LOLE.  Therefore, I chose a probability cutoff factor that would not allow N-3 autotransformer outages so I would have more computer time available to study more interesting network problems.

One important N-2 contingency allowed is one autotransformer out of service and one other circuit out of service.  This is allowed for circuits greater in length than 8.17e-6 = .02*(.0004+.00002*L), or rather L>0.4 miles.  The 3% electrical coupling cutoff test must also be satisfied, else the N-2 contingency will not be run.

PLF also provides for an increased probability for two and three circuits outaged simultaneously.  For example, the first entry in file COMM2 shows a double circuit 345 kV circuit 77.3 miles long from San Miguel to Marion.  Each circuit has an FOR = .0004+.00002*77.3 = .001946.  The common circuit FOR adder is .00001*77.3 = .000773.  This is added to the probability of random simultaneous outage of (.001946)2 = .0000038 to produce a common outage probability of .000777.  Dividing this common FOR by the sum of the two single circuit outages plus the common outage occurrences shows that common outages are expected to occur about 16.6% of the time.  The rest of the 83.4% of the time a single circuit outage will occur.  Note that these are long term outages of hours and possibly days, not relaying trips and reclosures for such things as lightning strikes.  The transmission FOR in the PLF reliability model represents equipment failures (or extended scheduled outages such that the circuit taken out of service cannot be restored when needed, even if there is an emergency condition).

The transmission FOR values used in this study are reasonable.  When developing these models a few years ago, I reviewed data used in other short courses, the IEEE journals, and circuit outage data from Austin and Houston.  I have seen data showing the mean time to failure of large EHV autos to be only 11 years!  I recall a conversation once with another engineer in which he said that every NERC meeting he attended had a discussion about how many autos had blown up since the last meeting.

Only 345/138 kV autos are outaged in this study (no 138/69 kV auto outages).  PLF shows that there are 153 345/138 kV autotransformers of 100 MVA or greater.  Using an FOR=.02 for autotransformers produces an average of 4 EHV transformers out of service at any time in ERCOT.  If ERCOT has more or fewer than this number, then the FOR should be changed to reflect what is actually occurring in the system.  Likewise, there are 239 EHV circuits greater than 900 MVA capacity.  Using the transmission FOR formula of .0004+.00002*L, there should be about 1.1 EHV circuits forced out of service in ERCOT on any day during peak hours in the summer.

The transmission FOR formula can be tuned to actual conditions by collecting a little bit of data.  The number of 345 kV circuits out of service (because of equipment failure) at the same time every afternoon, say 3 PM, is written down.  At the end of the summer the numbers are averaged.  Then the transmission FOR parameters are scaled such that the daily average produced by the model is the same as the average number of 345 kV circuits that are actually forced out of service in the system.  I have been told that there is usually one 345 kV circuit out of service in ERCOT, therefore, I think the formula used in this study is representative of the actual system performance.

Single Area Solution Methodology in Phases I and II:

- Generator unit MW and FORs (and DFORs) are put into a file, hourly load shapes in another file, the load forecast, and the load forecast uncertainty.

- Begin with a graph that looks like a rectangular box with the x axis from 0 to the sum of all MW generation and the y axis is the probability axis from 0 to 1.  Start with a curve having y=1 for all x < sum of all generation and y = 0 for x greater than the sum of all generation.

- Choose the next generator to outage.  Let this generator have an FOR of 15% and capacity of 100 MW as an example.  The convolution process is to scale the initial curve y values to .85 of their value with no shift left or right and then add that to the initial curve scaled to .15 of their values and shifted to the left by 100 MW.  Then add the .85 and the .15 scaled curves together to create a new y valued function.  The notched area in the upper right hand of the graph is the unserved demand and energy.  Probability represents an amount of time the generation is not in service.

- Repeat step 3 for all generators.

- Look up the probability of not being able to serve load every hour from the curve created in steps 3 and 4.  Unserved energy is the integral of the area above the curve from 0 to the MW load for that hour.

Graphical Explanation of the Phase I and II Solution Procedure:

Start by assuming generation is available 100% of the time as shown in the graph below.

100%

0%

Time

0

Generation MW

Total

Convolution of generation proceeds as shown on the next page.  The numerical examples are given to illustrate the procedure.

As an example, let 100 MW be forced out of service 20% of the time.

100%

0%

Time

0

Generation MW

Total

100 MW

= sum of a 20% shifted 100 MW graph  (   ) and an 80% not shifted graph  (    )

outaged

Then, let 200 MW be forced out of service 40% of the time.

= sum of a 40% 200 MW shifted graph (   ) and a 60% no shift graph (   )

100%

0%

Time

0

Generation MW

Total

200 MW shift

200 MW out of service

200 MW in service

Repeat this process until all the generators are outaged, producing the curve below.

100%

0%

Time

0

Generation MW

Total

unserved demand, energy, probability, and duration

Hourly MW Load

Transmission Constraints Solution Methodology in Phase III:

- Use the same generator data as the single area study plus a load flow raw data file.  Generators are given their bus number locations in the load flow data file.

- Repeat the single area convolution process, except this time, calculate incremental load flow powers based on the outage of each individual generator.  Create a probability curve for the MW flow on every transmission constraint.

- Identify the circuit with the greatest probability of overload and choose a small MW increment of this circuit to unload.

- Choose the generator and load area that will be used to remove this small overload increment.  Reduce their MW generation and load.  Collect loss of load statistics for the load area.  Recalculate all network circuit flows due to this increment and go back to step 3 to repeat the process until no more circuit overloads exist.

- Choose the next circuit to outage and repeat steps 2 through 4.  Each circuit outage state is a separate calculation from the beginning to the end of the process.

Graphical Explanation of the Phase III Solution Procedure:

A circuit flow due to only generators causing increased loading.

100%

0%

Time

0

Line Flow MW

Rating

positive flow gens - static load flow

random generator outages

ckt overload region

A circuit flow due to all generators with random outages.

100%

0%

Time

0

Line Flow MW

Rating

static load flow

line overload region

Σ All Gens

Σ Pos Flow Gens

In the previous graph, the circuit overload region is broken into several smaller MW increments.  Load areas and generators are identified that will be reduced in MW amount to remove the overloaded segment.  As each segment of overload is removed, the circuit flows on the other overloaded circuits are reduced.  Circuits are unloaded in decreasing sequence of the percent time of overload (i.e., highest probability of overload is selected).

Load shedding areas and generators are selected to remove a circuit overload.

gens

loads

Transmission Constraints for Circuit Outage States:

Circuit and transformer outage states are not a convolution process as they are in the modeling of generator outages.  Each transmission configuration is set up and solved as a separate set of loss of load calculations. More information about the solution procedures outlined in this report are given in the reference papers on web page

http://k5gp.home.texas.net/relstudy.htm.

Loss of Load Expectation in days per year (using daily peak demands).

The base case includes all combinations of generator outages.

N-0 = no circuits out, N-1 = all single contingencies, N-2 = double contingencies, N-3 = triple ckts out.

Probabilistic Load Flow.

Power Distribution Factor; the per unit power flowing in a circuit from a generator to a load area.

Expected Unserved Energy in MWH.  In this instance the test period is just one hour.