###### ERCOT STEADY STATE WORKING GROUP

###### PROCEDURAL MANUAL

##### February 9, 2001

ERCOT STEADY-STATE WORKING GROUP’S SCOPE

The ERCOT Steady-State Working Group (SSWG) operates under the direction of the Reliability and Operations Subcommittee (ROS). The SSWG’s main objectives are to produce seasonal and future load-flow base cases, coordinate tie-line data, update the Most Limiting Series Element Database, maintain the ERCOT Data Dictionary, update the SSWG Procedural Manual, prepare data for and review seasonal transmission loss factor calculation, and provide requested transmission system data and power-flow support documents to market participants. The SSWG usually meets in July and November to accomplish these tasks, and at other times during the year as needed to resolve any impending load-flow modeling issues or to provide technical support to the ROS. Some of the above responsibilities are further described as follows:

- Develop and maintain load-flow base cases for the spring, summer, fall, and winter seasons of the upcoming year. The cases, collectively known as Data Set A, are normally produced by the SSWG by August 1st on an annual basis. These seasonal cases consist of one on-peak and one off-peak case for each of the four seasons.

- Develop and maintain load-flow base cases for the five future years following the upcoming year. The cases, collectively known as Data Set B, are normally produced by the SSWG in December on an annual basis. These future cases consist of five summer on-peak cases, one winter on-peak case, and one minimum case.

- Maintain and update the ERCOT Data Dictionary to reflect new bus information and SCADA names. This task is performed during the Data Set A and B work.

- Maintain and update the SSWG Procedural Manual to reflect current planning practices and the latest load-flow base case modeling methodologies.

- Prepare data for and review seasonal transmission loss factor calculation on an annual basis. This task is to be done by October 1st.

- Maintain and update the Most Limiting Series Element Database to reflect the most limiting thermal ratings of transmission and substation equipment. This task is performed annually at year end.

- Assist in development of ERCOT processes for compliance with NERC Planning Standards for both entity and region-wide requirements.

- Coordinate tie-line data submission to ERCOT with neighboring companies. Maintain and update the ERCOT Tie-Line Database. This task is performed during the Data Set A and Data Set B work.

- Provide transmission system data, contingency information and power-flow support documents to market participants as requested by the Data Sharing Task Force.

- Perform Voltage Control and Reactive Planning studies as directed by the ROS.

Table of Contents

###### SECTION 1.0 – Data Requirements	4

1.1 	General 	5

1.2	Bus Data 	6

1.3	Load Data 	7

1.4	Generator Data	9

1.5	Line Data 	12

1.6	Transformer Data 	19

1.7	Static Reactive Devices 	23

1.8	Dynamic Control Devices 	25

###### SECTION 2.0 – Load-flow Procedures and Schedules	26

2.1	Data Set A Considerations 	27

2.2	Data Set B Considerations	29

2.3	Error Screening and Case Updates	31

###### SECTION 3.0 – Other SSWG Activities	34

3.1	Transmission Loss Factor Calculation (to be developed by ESPTO)	35

3.2	Voltage Control and Reactive Planning (to be determined)	35

###### APPENDICES 	36

A	Owner ID, TSP, Bus/Zone Range and Tables	37

B	Glossary of Terms	40

C	TSP Impedance and Line Ratings Assumptions	41

D	MLSE	62

E	Data Sharing Requirements	63

###### SECTION 1.0 – Data Requirements

1.1 GENERAL

The principal function of the SSWG is to provide analytical support of the ERCOT electrical transmission network from a steady state perspective.  To accomplish this, the Working Group performs three principal charges: load-flow, voltage control and reactive planning, and transmission loss factor calculation tasks.

    - Coordination with ERCOT Operations

- Load-flow base cases provide detailed representation of the electric system for planning

and evaluating the current and future high voltage electrical system and the effects of new loads, generating stations, interconnections, and transmission lines.

    - Model

- The model represents the high voltage system, branches, buses, bus components, impedances, loads, multi-section lines, ownership, switched shunts, transformers, DC lines and zones. The network model is combined at ERCOT System Planning Technical Operations (ESPTO) in the latest approved PTI PSS/E and rawd ASCII data format based on a 100 MVA base. The model should reflect expected system operation.

    - Data

The SSWG will take the load data from the ERCOT Annual Load Data Request (ALDR) and build two sets of cases, Data Set A and Data Set B (see Sections 2.1 and 2.2).

Data Set A consists of seasonal cases for the following year.  The SSWG must finalize Data Set A by early August to meet ERCOT’s schedule to perform the commercially significant constraint studies. Data Set B, which is finalized in mid-December, is used for planning purposes and consists of the following:

- Future summer peak planning cases

- A future winter peak planning case

- A future minimum load planning case

- ERCOT Data Dictionary

    - Load-flow Case Uses

- The cases being created each year are listed in Sections 2.1 and 2.2.  ESPTO and Transmission Service Providers (TSPs) test the interconnected systems modeled in the cases against the ERCOT Planning Criteria to assess system reliability in the coming year and into the future. SSWG cases are used as the basis for many other types of calculations and studies by ROS Working Groups and ERCOT System Operations such as:

- Internal planning studies and generation interconnection studies

- Voltage control and reactive planning studies

- Dynamics Working Group stability studies

- ERCOT transmission loss factor calculation

- Basis for ERCOT operating cases and FERC 715 filing

- Commercially significant constraints studies

1.2 BUS DATA

    - Areas defined by TSP

Defined areas have been added to the ERCOT load-flow cases for modeling convenience and are denoted in the TSP Bus/ Zone Range Table in Appendix A.

    - Bus Data Records

All in-service transmission (60kV and above) and generator terminals shall be modeled in load-flow cases. Each data bus record has a bus number, name, base kV, bus type code, real component of shunt admittance, reactive component of shunt admittance, area number, zone number, per-unit bus nominal voltage magnitude, bus voltage phase angle, and owner id.

    - Bus Ranges

Presently, ERCOT is modeled within a 100,000 bus range. Bus ranges, new or amended, are allocated by the Chairman of the SSWG with confirmation from the SSWG members.  Bus ranges are based on high-side bus ownership. (Refer to TSP Bus/Zone Range Table in Appendix A)

Bus numbers from within the TSP’s designated bus range are assigned by the TSP and are to remain in the assigned ranges until the equipment or condition that it represents in the ERCOT load-flow cases changes or is removed.

    - Zone Ranges

Presently zone ranges, new or amended, are allocated by the Chairman of the SSWG with confirmation from SSWG members. Each TSP represents their network in the ERCOT load-flow cases using allocated zone ranges. Zone numbers that have been assigned by the TSP, within the TSP’s designated zone range, may be changed by the TSP as needed to represent their network in the ERCOT load-flow cases. Every zone number assigned must be from the TSP’s designated zone range. Zone identifiers are specified in zone data records.  Each data record has a zone number and a zone name identifier. (Refer to TSP Bus/Zone Range Table in Appendix A)

    - Owner IDs

All TSPs must provide owner IDs for buses. This data is maintained in the Owner ID, TSP Bus/Zone Range Table shown in Appendix A.

    - Bus Name

As of April 1, 2000, bus names shall not identify the customers or owners of loads or generation at new buses unless requested by customers.

1.3 LOAD DATA

Each bus modeling a load must contain at least one load data record.  Each load data record contains a bus number, load identifier, load status, area, zone, real and reactive power components of constant MVA load, real and reactive power components of constant current load, and real and reactive power components of constant admittance load.  All loads (MW and MVAR) should be modeled on the high side of transformers serving load at less than 60 kV.

Guidelines:

    - The bus number in the load data record must be a bus that exists in the base case. As of 2001 owner IDs shall not be associated with any entity in cases.

    - The load identifier is a two-character alphanumeric identifier used to differentiate between loads at a bus. Self-serve loads greater than 50 MW must be identified by “SS.” See Section 1.4.1. Partial self-serve load should be modeled as a multiple load with “SS” identifying the self-serve portion. Distributed generation less than 10 MW must be identified by “DG” and modeled as negative load.

    - The load data record zone number must be in the zone range of the TSP serving the load.  It does not have to be the same zone that the bus is assigned to.   Zone only describes a group of buses for study.

    - Loads in ERCOT may be modeled by any combination of constant MVA, constant current, and constant admittance.  How the load is represented does not matter for a steady-state solution where voltages are generally close to normal operating levels.

For steady-state solutions, loads are normally treated as constant MVA because it is impractical to differentiate between them.  However, for dynamic conditions loads behave differently from one another and the loads must be modeled with different characteristics to achieve correct study results.  Load behavior can be placed in three different categories, as constant MVA, constant current or constant admittance.

As voltage changes, real and reactive power will remain constant above some threshold voltage set point for constant MVA loads.  Current will remain constant during voltage fluctuations above a threshold voltage for constant current loads.  Current will change proportionally to the voltage above a threshold voltage for constant admittance loads.  Values for the three load types should be modeled as MW and MVAR in the base case.

    - MVAR load modeled at each bus shall include transformer losses.  It is extremely important that loads reflect correct power factors on the high side of transformers serving load at less than 60 kV.  MW transformer losses are very small; however, MVAR losses, for example, may change the power factor from .98 at the low-side terminals to .96 at the high side.  Incorrect reactive modeling perpetuated throughout a wide area might result in real world voltage problems being ignored.  MVAR loads shall be calculated from power factors provided in the Annual Load Data Request (ALDR).  MVAR transformer losses shall be calculated from this load level assuming the ALDR given load and power factor at the high side of the substation transformer.

    - Generator auxiliary load should not be modeled at generating station buses. Refer to section 1.4.1.

    - The system load for the load serving entities should be obtained from the load serving entities’ ALDR.

    - Multiple loads from different TSPs at a bus may be used. At this time, each TSP can define a load however it wishes with a load ID of its choice though careful coordination is required between TSP representatives to ensure that the loads at the bus get modeled correctly.

    - Interruptible loads should be included in the total load modeled.

1.4 GENERATOR DATA

    - Acquisition of Generator Data

- Only net real and reactive generator outputs and ratings should be modeled in load-flow cases. Net generation is equal to the gross generation minus station auxiliaries and other internal power requirements.  All non-self-serve generation connected at 60kV and above with at least 10 MW aggregated at the point of interconnect must be explicitly modeled. A generator explicitly modeled must include generator step-up transformer and actual no-load tap position. Generation of less than 10 MW is still required to be modeled, but  not explicitly.

- Self-serve generators serve local load that does not flow through the ERCOT transmission system. Data should be submitted for self-serve facilities for:

- Any generating unit or plant with gross real power output of at least 50 MW.

- Any self-serve loads with a contract of at least 50 MW of backup power.

      - Coordination with Power Generating Companies

- Power Generating Companies shall provide the following information:

- Data forms from the ERCOT Generation Interconnection Procedure

- One-line electrical system drawing of the generator’s network and tie to TSP (or equivalent)

- Modeling information of the generator’s transmission system in PTI or GE format

- Units to be retired or taken out for maintenance

      - Coordination with other ERCOT Working Groups

- All generator data should be coordinated with the Dynamics Working Group and System Protection Working Group members to assure that it is correct before submitting the cases. This will insure that all of the cases have the most current steady state and dynamics information.  The following are items that should be coordinated:

- Unit bus number

- Unit ID

- Unit maximum and minimum real power capabilities

- Unit maximum and minimum reactive power capabilities

- Unit MVA base

- Resistive and reactive machine impedances

- Resistive and reactive generator step-up transformer impedances

      - Coordination with ERCOT Operations

- The following data should be coordinated with ERCOT Operations:

- ERCOT historical generation dispatch

- Units real and reactive test data

- Unit outage schedules

    - Review Expected Load for Area to Serve

Before the generation schedule can be determined, the expected area load and losses (demand) must be determined. Each MW of demand needs to be accounted for by a MW of generation. The ALDR should be used for all the Data Set A and B cases.

    - Generation Dispatch Methodology

In order to simulate the future market, the following methodology was adopted for building the seven 2002 Data Set B cases (SS03sum1, SS04sum1, SS05sum1, SS06sum1, SS07sum1, SS05min, and SS05win1).

Units owned by the Non-Opt-In Entities (NOIE) were dispatched according to the NOIE's planning departments. Unless contracts are known for the full output of a unit, all remaining MWs of NOIE units will be put into the ERCOT dispatch in their respective order.

Self-serve generation was also dispatched independently. It is believed that cogeneration and self-serve units will have a better financial incentive to run than other plants. These plants were turned on at full output unless actual data was available, in which case they were dispatched to an average of their historical output. DC Ties were put at previous levels, which is the best available information.

All other units were placed in a spreadsheet and sorted by a predefined commitment order (COMMORDER) to create an economic dispatch order. Each COMMORDER is sorted by age with newer plants being placed on top. Generation was turned on to meet the load levels of each case.

The unit commitment order is as follows:

- Exceptions (Units that can operate in more than one region are dispatched at 50% of PMAX (Tenaska Frontier and Gateway), voltage support units (documentation is posted showing voltage problem), DC ties, and must run if any exist under ERCOT protocols)

- NOIE dispatch (Commorder number is not always 2 for NOIE units. It can be another number that may better match with the unit)

- Nuclear - max MW

- Coal (bituminous, sub-bituminous, lignite) - max MW. Existing units and future units that are expected to be constructed. Future units will be dispatched prior to existing units if it can be assumed that they will be more efficient.

- Hydro (most recent information). Existing units and future units that are expected to be constructed. Future units will be dispatched prior to existing units if it can be assumed that they will be more efficient.

- Other renewable – Wind at 10%and 20% in on-peak and off-peak cases, respectively; solar max MW, methane max MW - less than 10 MW is modeled as negative load. Existing units and future units that are expected to be constructed. Future units will be dispatched prior to existing units if it can be assumed that they will be more efficient.

- Self-serve. Existing units and future units that are expected to be constructed. Future units will be dispatched prior to existing units if it can be assumed that they will be more efficient.

- Cogeneration.  Existing units and future units that are expected to be constructed. Future units will be dispatched prior to existing units if it can be assumed that they will be more efficient.

- Combined cycle. Existing units and future units that are expected to be constructed.  Future units will be dispatched prior to existing units if it can be assumed that they will be more efficient.

- Base load natural gas (steam through boiler). Existing units and future units that are expected to be constructed.  Future units will be dispatched prior to existing units if it can be assumed that they will be more efficient.

- Cycling natural gas (steam through boiler). Existing and future units that are expected to be constructed.  Future units will be dispatched prior to existing units if it can be assumed they will be more efficient

- Peaking gas (steam through boiler). Existing and future units that are expected to be constructed.  Future units will be dispatched prior to existing units if it can be assumed they will be more efficient

- Combustion turbine – simple cycle. Existing and future units that are expected to be constructed.  Future units will be dispatched prior to existing units if it can be assumed they will be more efficient

If a future unit is not on the ERCOT generation web site, it will not be put in the case unless an agreement has been reached between the TDSP and IPP to do so. Future units that are expected to be constructed must either have signed an SGIA or have provided an agreement to reimburse the TSP for expenses incurred toward constructing facilities for their generation if the generation project fails to go forward.

    - Voltage Profile Adjustments

      - Schedule Voltage for Generator Units

- After generation has been determined, the next step is to set the proper voltage profile for the system. The location and output of the generators is important to the voltage stability of the system. Knowing how the operators set the voltages and monitor the VAR flow will present a more realistic case.

      - Voltage Control

- Check the voltages at several key locations within the system when modifying generation voltage and control VARS.  When these voltages are not within acceptable parameters, changes in the system VARS are needed. VAR changes can be accomplished by turning on/turning off capacitors or reactors, and by adjusting the voltage at certain generators and transformer taps.

1.5 LINE DATA

    - Use of Load-flow Data Fields

      - Bus Specifications

The end points of each branch in the ERCOT load-flow case are specified by “from” and “to” bus numbers.  In most cases the end point buses are in the same TSP area.  However, when the “from” and “to” buses used to specify a branch are in different TSP areas, the branch is considered to be a tie line (See Section 1.5.3, Coordination of Tie Lines). Branch data includes exactly two buses. The end points of Multi-Section Lines (MSL) are defined by two buses specified in a branch data record.  (See 1.5.2.) There are other components that are modeled with more than two buses, such as transformers with tertiaries that may be represented by three-bus models.

      - Circuit (Branch) Identifier

Circuit identifiers are limited to two alphanumeric characters.  Each TSP will determine its own naming convention. These identifiers are typically numeric values (e.g. 1 or 2) that indicate the number of branches between two common buses, but many exceptions exist.

      - Impedance Data

The resistive and reactive impedance data contained in the load-flow cases are both expressed in per-unit quantities that are calculated from a base impedance. The base impedance for transmission lines is calculated from the system base MVA and the base voltage of the transmission branch of interest.  The system base MVA used in the ERCOT load-flow cases is 100 MVA (S = 100 MVA).  The base voltage for a transmission line branch is the nominal line-to-line voltage of that particular transmission branch.  (See Transformer Data for Calculation of Transformer Impedances.) I didn’t see a section called this. Therefore the base impedance used for calculating transmission branch impedances is:

ohms

This base impedance is then used to convert the physical quantities of the transmission line into per-unit values to be used in the load-flow cases.

        - Resistance

Once the total transmission line resistance is known and expressed in ohms, then this value is simply divided by the base impedance to obtain the per-unit resistance to be entered in the load-flow case.  This calculation is as follows:

        - Reactance

Once the total transmission line reactance is known and expressed in ohms, then this value is also divided by the base impedance to obtain the per-unit reactance to be entered into the load-flow case.  This calculation is as follows:

        - Charging

Line charging is expressed as total branch charging susceptance in per unit on the 100 MVA system base.  The total branch charging is expressed in MVARs and divided by the system base MVA to get per unit charging.  The equation used to accomplish this depends on the starting point. Typically the charging of a transmission line is known in kVARs.  Given the total transmission line charging expressed in quavers, the equation to calculate the total branch charging susceptance in per unit on the system base is as follows:

Or, given the total capacitive reactance to neutral expressed in ohms , the equation to calculate the total branch charging susceptance in per unit on the system base is as follows:

      - Facility Ratings

ERCOT load-flow cases contain fields for three ratings for each branch record.  The ratings associated with these three fields are commonly referred to as Rate A, Rate B and Rate C.  Methodology used by each TSP shall be kept current in Appendix C. Following are the ERCOT facility ratings definitions:

        - Ratings Definitions

Rate A  – Normal Rating

The most limiting series element (MLSE) rating at which a transmission facility can operate for an indefinite period of time without exceeding NESC clearances or experiencing unacceptable loss of life or equipment failure.

Rate B  – Emergency Rating

The most limiting series element (MLSE) rating at which a transmission facility can operate for the time sufficient for adjustment of transfer schedules, generation dispatch or line switching in an orderly manner without exceeding NESC clearances or experiencing unacceptable loss of life or equipment failure.

Rate C  – Conductor/Transformer Rating

The rating at which the conductor can operate for an indefinite period of time without exceeding NESC clearances or the transformer can operate for an indefinite period of time without experiencing unacceptable loss of life.

When performing security studies, ESPTO will default to Rate B, unless the TSP has previously indicated in writing that other ratings (e.g., Rate A) should be used.  If problems exist using Rate B and Rate B is significantly different from Rate C, then ESPTO will contact the TSP.

        - NERC Planning Standards

Compliance with the NERC Planning Standards for facility ratings is required in the ERCOT load-flow cases.  Specifically, these ratings should be in compliance with NERC Planning Standard Measures, which state,  "The rating of a system facility (transmission line, transformer, etc.) shall not exceed the rating of the most limiting series element (MLSE) in the circuit or path of the facility, including terminal connections and associated equipment."  "In cases where protection systems and control settings constitute a loading limit on a facility, this limit shall become the rating for that facility."  “Coordinated ratings for jointly owned facilities shall be documented in a document or database.  Joint owners shall agree on the ratings.” NERC Standards require that “Facility owners shall have on file a document or data base identifying the normal and emergency ratings of all of their electrical facilities (e.g., lines, terminal equipment, and transformers) that impact the bulk interconnected transmission system.

        - Most Limiting Series Element Database

MLSE database contains ratings of all existing elements in series (switches, current transformers, conductors, etc.) between the two end terminals of a transmission line and provides the maximum rating of the transmission line. This data is due to ESPTO with the Data Set A work each year. See Appendix D for example output.

      - Branch and Transformer Adjustment Data Record Coordination

Branch data records are used both for transmission lines and transformers. For every transformer adjustment (LTC) data record, there must also exist a branch record modeled as a transformer with the same from-bus, to-bus and circuit ID. (See Transformer Data section for more details on transformer data.)

      - Complex Admittance

Branch Data records include four fields for complex admittance for line shunts.  These records are rarely used in ERCOT.

      - Status

Branch data records include a field for branch status.  Entities are allowed to submit branch data with an out-of-service status for equipment normally out of service.  This information will be kept throughout the load-flow data preparation process and returned to all entities with the final ERCOT load-flow cases.

      - Line Length and Ownership

        - Mileage and Ownership Data

This data should be provided.

        - Ownership

The load-flow database allows users to specify up to four owners for each branch including percent ownership. Ownership and owner IDs should be included for all non-transformer branches including transmission lines owned by generation entities.  The percent ownership of each line should sum up to 100%. See Appendix A.

        - Practices for Verification

Transmission line length should be verified from field data before values are entered into the load-flow data.  The following equation is an approximation that applies to transmission lines that are completely overhead:

or assuming   MVA then

    - Multi-Section Line Grouping

A multi-section line is defined as a grouping of several previously defined branches into one long circuit having several sub-sections or segments.

Example: Two circuits exist (Figure 1) which originate at the same substation (4001) and terminate at the same substation (4742).  Each circuit has a tap to Substation A and a tap to Substation B.  If a fault occurs or maintenance requires an outage of Circuit 09, the circuit would be out-of-service between bus 4001 and bus 4742 including the taps to buses 4099 and 4672.  The loads normally served by these taps would be served by means of low-side rollover from buses 4100 and 4671 on Circuit 21.  This is the type of situation for which multi-section lines are used to accurately model load flows.

Figure 1.  Example of circuits needing to use multi-section line modeling.

Figure 2 represents a load-flow data model of the circuits in Figure 1.  Branch data record would have included  the following:

4001,4099,09,…

4099,4672,09,…

4672,4742,09,…

4001,4100,21,…

4100,4671,21,…

4671,4742,21,…

along with the necessary bus, load, and shunt data.  To identify these two circuits as multi-section lines, entries must be made in the raw data input file.  The multi-section line data record format is as follows:

I, J, ID, CKT1, DUM1, CKT2, DUM2, ... CKT9, DUM9, CKT10

where:

I  	“From bus” number.

J  	“To bus” number.

ID  	Two character multi-section line grouping identifier. The first character must be an ampersand (“&”). ID = ‘&1’ by default.

CKTi 	Branch circuit identifiers of branches that are members of this multi-section line grouping. CKTi = ‘1’ by default.

DUMi 	Bus numbers, or extended bus name enclosed in single quotes, of the “dummy buses” connected by the branches that comprise this multi-section line grouping. No defaults allowed.

Each dummy bus must have exactly two branches connected to it, both of which must be members of the same multi-section line grouping.

The statuses of line sections are set such that the multi-section line is treated as a single element.

Figure 2. Load-flow model of example circuits.

For our example, the following would be entered as multi-section line data records:

4001, 4742, &1, 09, 4099, 09, 4672, 09

4001, 4742, &2, 21, 4100, 21, 4671, 21

Multi-section lines give a great amount of flexibility in performing contingency studies on load-flow base cases.  When set up correctly, hundreds of contingencies where the automatic low-side load rollover occurs can be analyzed and reported within minutes.

    - Coordination of Tie Lines

A tie line is a branch that connects two control areas in the load-flow case. Normally the bus at one end of the tie line is in one control area and the bus at the other end is in another control area. Each of the interconnected TSPs owns some terminal equipment or line sections associated with the tie line.  The branch may be a transmission line, transformer, bus section or another electrical component connecting systems together.

Careful coordination and discussion is required among SSWG members to verify all modeled tie-line data. Even in load-flow cases where no new tie lines were installed, there could be many tie-line changes. Construction timings of future points of interconnection can change. As an example, a tie line may need to be deleted from a spring case and added to a summer case. Another example is, if a new substation is installed in the middle of an existing tie line, it redefines the tie-line bus numbers, mileages, impedances and possibly ratings and ownership.

Tie branch models also affect a number of important ERCOT calculations and therefore must accurately reflect real-world conditions. Also missing or erroneous ties can produce unrealistic indications of stability and/or voltage limits. Inaccurate metering points, impedances, ratings, transformer adjustment data, status information, mileages, or ownership data can all have a profound effect on system studies; therefore it is imperative that neighboring entities exercise care in coordinating tie branch data.

    - Metering Point

Each tie line or branch must have a designated metering point and this designation should also be coordinated between neighboring control areas.  The location of the metering point determines which control area will account for losses on the tie branch.  The load-flow program allocates branch losses to the control area of the un-metered bus.  For example, if the metering point is located at the “to” bus then branch losses will be allocated to the control area of the “from” bus.

The first bus specified in the branch record is the default location of the metering point unless the second bus is entered as a negative number. These are the first and second data fields in the branch record.

    - Tie-Line Ratings

Ratings for tie lines should be mutually agreed upon by all involved entities and should comply with NERC Planning Standards: “Ratings of jointly-owned facilities shall be coordinated and provided on a consistent basis.”

    - Coordination of Tie-Line Data Submission

It is imperative for neighboring entities to coordinate tie data in order to allow Data Set A and Data Set B work activities to proceed unimpeded. Entities should exchange written documents detailing tie-line data at least two weeks before the data is due to ESPTO. Coordination of tie data includes timely agreement between entities on the following for each tie line:

- In-service/ out-service dates for ties

- Metering point bus number

- From bus number

- To bus number

- Circuit identifier

- Impedance and charging data

- Ratings

- Transformer adjustment (LTC) data

- Status of branch

- Circuit miles

- Ownership (up to four owners)

- Entity responsible for submitting data

1.6 TRANSFORMER DATA

    - Transformer Modeling Records

Transformers modeled in ERCOT load-flow cases are specified by three sets of data records: Branch Data; Transformer Adjustment Data and Transformer Impedance Correction Tables.

    - Branch Data – Transformers

The first sets of records for transformer modeling are contained in the set called Branch Data and include the same fields as defined in Section 1.5, Line Data.

      - Bus Numbers

The end points of each transformer branch in the ERCOT load-flow case are specified by “from” and “to” bus numbers.  The “from” bus is the bus connected to the tapped side of the transformer and the “to” bus is connected to the impedance side of the transformer being modeled. In some cases, the “from” and “to” buses used to specify a branch are in two different control areas, making the branch a tie line (See Section 1.5.3, Coordination of Tie Lines). The “from” bus is the metered side of the transformer by default, but can be assigned to the other bus by assigning a negative number to the second bus. The metered side determines which control area losses due to the transformer are assigned to (control area of the un-metered bus). Three winding transformers (transformers with tertiaries) may be represented by multiple branch records with buses defined at each transformer terminal.

      - Branch Identifier

Circuit identifiers are limited to two alphanumeric characters. Actual transformer identifiers may be used for circuit identifiers for transformers, however, typically, circuit identifiers are used to indicate which transformer is being defined when more than one transformer is modeled between two common buses.

      - Impedance Data

The resistance and reactance data for transformers are specified in the load-flow database in per-unit quantities on a 100 MVA system base, as described in Section 1.5.1.3, Impedance Data, in the line data chapter.

        - Resistance

Transformer test records should be used to calculate the resistance associated with a transformer branch record. As indicated above, the resistance calculated must be converted to a per-unit quantity on the system base. Where transformer test records are unavailable, the resistance should be entered as zero.

        - Reactance

Transformer test records or transformer nameplate impedance should be used to calculate the reactance associated with a transformer branch record. Where the transformer resistance component is known, the transformer impedance is calculated on the same base using the known data and the reactance component is determined using the Pythagorean theorem. Where the transformer resistance is assumed to be zero, the calculated transformer impedance can be assumed to be equal to the transformer reactance.

        - Susceptance

For load-flow modeling purposes, the transformer susceptance is always assumed to be zero.

      - Transformer Ratings

The ratings used for transformer branches are defined the same as in Section 1.5.1.4, Facility Ratings.

      - Tap Ratios

The ratio is defined as the transformer off-nominal turns ratio and is entered as a non-zero value in per unit. If no number is entered for Ratio, the load-flow program will erroneously treat the branch as a transmission line.  Where the base kV contained in the bus data records for the buses connected to transformer terminals are equal to the rated voltage of the transformer windings connected to those terminals, the transformer off-nominal ratio is equal to 1.00. When the transformer has no-load taps, the transformer off-nominal ratio will be something other than 1 and usually in the range of 0.95 to 1.05. The effects of load tap changing (LTC) transformer taps are handled in the transformer adjustment data record. Actual no-load tap settings will be periodically requested by ERCOT.

      - Angle

The transformer phase shift angle is for phase shifting transformers only and is measured in degrees from the untapped to the tapped side of the transformer. The angle is entered as a positive value for a positive phase shift.

      - Complex Admittance

Complex admittance data is not required for ERCOT load-flow cases and the values for each of these four fields should all be zeros.

      - Length

Circuit mileage has no meaning in a transformer branch record and should be entered as zero.

      - Status

This field indicates the status of the transformer. A value of 1 indicates the transformer is in-service and a value of zero indicates the transformer is out-of-service.

      - Ownership

The load-flow case allows users to specify up to four owners for each branch including percent ownership. Ownership and owner IDs should be included for all non-transformer branches. The sum of all percent ownerships should equal 100% for every line.

    - Transformer Adjustment Data

This second set of records for transformers establishes the control parameters for the automatic adjustment of transformer load tap changers and phase shifters. Only those branch records that are designated as transformers (non-zero ratios assigned) may be specified in a transformer adjustment data record. Transformer adjustment data should be modeled as transformers are normally operated. Transformers for which no tap adjustment data is provided are assigned default values that cause the transformer to be treated as a fixed ratio (non-LTC) transformer.

      - Branch and Transformer Adjustment Data Record Coordination

Branch data records are used both for transmission lines and transformers. For every transformer adjustment (LTC) data record, there must also exist a branch record modeled as a transformer with the same “from” bus, “to” bus and circuit ID.

      - Controlled Bus

The bus number of the bus whose voltage is controlled by the transformer LTC and the transformer turns ratio adjustment option of the load-flow solution activities. This record should be non-zero only for voltage controlling transformers.

      - Transformer Adjustment Limits

These two fields specify the upper and lower limits of the transformer turns ratio adjustment or phase shifter adjustment.  For transformers with automatic adjustment, they are typically in the range 0.80 to 1.20.

        - Upper Limit

This field defines the maximum upper limit of the off-nominal ratio for voltage or reactive controlling transformers and is entered as a per-unit value. The limit should take into account the no-load tap setting of the transformer, if applicable. For a phase shifting transformer, the value is entered in degrees.

        - Lower Limit

Similar to the upper limit, this field defines the lower limit of the off-nominal ratio or phase shift angle for the transformer defined.

      - Voltage or Load-Flow Limits

These two fields specify the upper and lower voltage limits at the controlled bus or for the real or reactive load flow through the transformer at the tapped side bus before automatic LTC adjustment will be initiated by the load-flow program. As long as bus voltage is between the two limits, no LTC adjustment will take place.

        - Upper Limit

This field specifies the upper limit for bus voltage in per unit at the controlled bus or for the reactive load flow in MVAR at the tapped side bus. For a phase shifting transformer, this field specifies the upper limit for the real load flow in MW at the tapped side bus.

        - Lower Limit

Similar to the upper limit, this field specifies the lower limit for the bus voltage or the real or reactive load flow for the transformer defined.

      - Step

Transformer turns ratio step increment for LTC is defined by this field and entered in per unit. Most LTC transformers have 5/8% or 0.00625 per unit tap steps.

      - Table

The number of a transformer impedance correction table is specified by this field if the transformer's impedance is to be a function of either the off-nominal turns ratio or phase shift angle. ERCOT load-flow cases normally don’t use these tables and this field is set to zero by default.

      - Control Enable

This field enables or disables automatic transformer tap adjustment. Setting this field to one enables automatic adjustment of the LTC or phase shifter as specified by the adjustment data values during load-flow solution activities. Setting this field to zero prohibits automatic adjustment of this transformer during these activities.

      - Load Drop Compensation

These two fields define the real and reactive impedance compensation components for voltage controlling transformers. They are ignored for MW and MVAR flow controlling transformers. ERCOT load-flow cases normally don’t use these fields and they are set to zero by default.

      - Resistive Component

The resistive component of load drop compensation entered in per unit is based on the resistance between the location of the LTC and the point in the system at which voltage is to be regulated.

      - Reactive Component

Similar to the resistive component of load drop compensation, this value is entered in per unit and is based on the reactance between the location of the LTC and the point in the system at which voltage is to be regulated.

    - Transformer Impedance Correction Tables

Used to model a change in transformer impedance as off-nominal turns ratio or phase-shift angle is adjusted in the load-flow solution.  Applied only when the table field in the transformer adjustment record (see Section 1.6.2.7) is set to a non-zero value. Is Section 1.6.2.7 the correct reference?

      - Table Number

The number of the transformer impedance correction table specified in the table field of the transformer adjustment record.

      - Off-Nominal Turns Ratio

The initial off-nominal transformer turns ratio in per unit or the phase-shift angle in degrees.

      - Impedance Scaling Factor

The scaling factor by which the transformer nominal impedance is to be multiplied to obtain the actual transformer impedance for the corresponding off-nominal turns ratio or phase- shift angle.

1.7 STATIC REACTIVE DEVICES

Presently all shunt reactors and capacitors that are used to control voltage at the transmission level are to be modeled in the ERCOT load-flow cases to simulate actual transmission operation. There are two distinct static reactive devices currently represented in the ERCOT load-flow cases: bus shunts and series compensated capacitors.  For ease of identifying all capacitive shunt devices in the ERCOT load-flow cases shunt devices are modeled as switched shunts.

    - Switched Shunt Devices

      - Bus Shunt

A shunt capacitor or reactor connected to the high side or low side of a substation transformer in a substation should be represented in the ERCOT load-flow case as a switched shunt device to accurately simulate operating conditions. It is required when modeling a fixed bus shunt that they be modeled with the switched shunt data record for easy identification in the ERCOT load-flow cases.

When a switched capacitor or reactor is submitted as the switched shunt data record, there are three modes that it can operate in: fixed, discrete, or continuous.  Switched capacitors are to be modeled in the fixed mode for the ERCOT cases with Vhi = 1.5 p.u. and Vlo = 0.5 p.u.

A switched shunt can be represented as up to eight blocks of admittance, each one consisting of up to nine steps of the specified block admittance. The switched shunt device can be a mixture of reactors and capacitors.  The reactor blocks are specified first in the data record (in the order in which they are switched on), followed by the capacitor blocks (in the order in which they are switched on). The complex admittance (p.u.), the desired upper limit voltage (p.u.), desired lower limit voltage (p.u.), and the bus number of the bus whose voltage is regulated must be defined to accurately simulate the switched shunt device.

If the load-flow program cannot handle the switched shunt modeling, then a fixed shunt capacitor or reactor could alternately be submitted on the bus data with the real component of shunt admittance entered as MW at one per unit voltage (nominal value) and the reactive component of shunt admittance entered MVAR at one per unit voltage. A positive reactive component of admittance represents a shunt capacitor and a negative reactive component represents a shunt reactor.

      - Dummy Bus Switched Shunt

If a capacitor or reactor were connected to a transmission line instead of a bus, an outage of the transmission line would also cause the capacitor or reactor to be taken out of service (see Figure 3).  For these instances, the most accurate model is the switched shunt modeled at a dummy bus connected by a zero impedance branch to the real bus.  This dummy bus must have exactly two branches connected to it, both of which must be members of the same multi-section line grouping.  The status of the line section is that the multi-section line is treated as a single element.   A capacitor or reactor connected to a line but modeled as a bus shunt will result in load-flow calculations for contingencies that differ from real operating conditions.

Figure 3. Example one-line of line connected capacitor bank

    - Series Compensated Capacitor Banks

Additional requirements will be developed in the future.

1.8 DYNAMIC CONTROL DEVICES

Certain transmission devices are planned and designed to provide dynamic control of electric system voltage/reactive parameters and are usually employed as solutions to specific system performance issues. They typically involve feedback control mechanisms using power electronics to achieve the desired electric system dynamic response. Examples of such equipment and devices include HVDC links, active or real load-flow control and reactive power compensation devices using power electronics, like unified load-flow controllers (UPFC’s), static var compensators (SVC’s), thyristor-controlled series capacitors (TCSC’s) and, in some cases, mechanically-switched shunt capacitors and reactors.  In planning and designing transmission control devices, it is important to consider their operation within the context of the overall interconnected systems over a variety of operating conditions. These control devices can be used to avoid degradation of system performance and cascading outages of facilities. If not properly designed, the feedback controls of these devices can become unstable during weakened system conditions caused by disturbances and lead to undesirable interactions with other controls in the interconnected systems.

    - Standards

Transmission control devices shall be planned and designed to meet the system performance requirements as defined in the NERC Planning Standards, Section I.A. and associated Table I. These devices shall be coordinated with other control devices within ERCOT and, where appropriate, with neighboring regions.

Typical one line diagram

    - HVDC Modeling Requirements

All dynamic control devices in current operation or planned for the future shall be modeled in load-flow cases. Modeling of dynamic control devices should not create solution problems or abnormal conditions in the load-flow cases. Further requirements are yet to be developed.

For generation and loads, the area desired interchange level shall be manually set and the area slack bus allowed to automatically adjust to this level plus losses. Capacitors, filter banks and reactors shall be added or removed based on normal DC tie operation. Real power shall be the net of all transactions to the HVDC tie and reactive power is calculated as a percentage of real power, as in actual operation. Use of the interim unplanned loss matrix methodology requires that neither generation nor load be equal to zero.

###### SECTION 2.0 – Load-Flow Procedures and Schedules

2.1 DATA SET A CONSIDERATIONS

The detailed data requirements for the production of the load-flow cases by ESPTO are described in other sections of these guidelines.  This section presents a general overview of the items that should be considered when preparing ERCOT load-flow data.

    - Data Set A Uses

The ‘Data Set A’ cases are used for short-term planning, system operations analysis, commercially significant constraint determination, and transmission loss factor calculations. Data Set A cases are submitted by the ERCOT region in response to FERC 715 requirements and are posted on ERCOT web site for general use.

    - Data Set A Case Definitions

Load-flow cases produced by ESPTO are to be divided into two groups.  The first group, “Data Set A,” models expected conditions for the following year’s four seasons (eight cases).  The second group, “Data Set B,” models cases for the five-year planning horizon.

Data Set A seasons are as follows:

SPG		March, April, May

SUM		June, July, August, September

FAL		October, November

WIN		December, January, February

ERCOT DATA SET A BASECASES

(YR) = FOLLOWING YEAR

| BASE CASE | # NOTES | TRANSMISSION IN-SERVICE DATE |
| --- | --- | --- |
| (YR)SPG1 | 2 | April 1, (YR) |
| (YR)SPG2 | 3 | April 1, (YR) |
| (YR)SUM1 | 1 | July 1, (YR) |
| (YR)SUM2 | 3 | July 1, (YR) |
| (YR)FAL1 | 2 | October 1, (YR) |
| (YR)FAL2 | 3 | October 1, (YR) |
| (YR+1)WIN1 | 1 | January 1, (YR+1) |
| (YR+1)WIN2 | 3 | January 1, (YR+1) |

## Notes

- Cases to represent the maximum expected load during the season.

- Cases to represent maximum expected load during month of transmission in-service date.

- Cases to represent lowest load on same day as the corresponding seasonal case  (not a minimum case). For example, (YR)FAL2 case represents the lowest load on the same day as the (YR)FAL1 case.

    - Entity Responsibilities

The Data Set A load-flow cases are assembled and produced by ESPTO.  The responsibilities for providing this data are divided among the various market participants. These data provision responsibilities may overlap among the various market participants because participants may designate their representative or a participant may be a member of more than one market participant group.  The market participants can generally be divided into four groups: TSPs, Load Serving Entities, Power Generating Companies, and Marketing Entities.  The data responsibilities of each group are as follows:

      - TSPs

It is the responsibility of the TSPs to provide all the data required to model the transmission system (line impedances, ratings, transformers, reactive sources, etc.) This will include data for all generator step-up transformers physically tied to the system of the TSP.  Transmission providers may also be responsible for load or generation data if they are the designated representatives for load entities or power generating companies.

      - Load Serving Entities

It is the responsibility of the load serving entities or their designated representatives to provide the data required to model the loads including the data provided in the ALDR in all cases. This data should be coordinated with their respective TSPs.

      - Power Generating Companies

It is the responsibility of the generation entities to provide all data required to model the generators in all the cases. See Section 1.4. This data should be coordinated with their respective TSPs and should include but is not limited to unit capabilities.

      - Marketing Entities

It is the responsibility of marketers to supply the load and/or generation data if they are the designated representatives for either a load or generating entity or both.

    - Schedule

ESPTO shall post all data and information. As an example:

March 1	ALDR due to ESPTO

April 1		ALDR due to SSWG

April 24	NOIEs send generation dispatch data to ESPTO

May 1		Raw data files due to ESPTO

May 8		Pass 1 cases due to SSWG

May 10	SSWG general meeting if needed

May 20 	Pass 1 changes due to ESPTO

May 27	Pass 2 cases due to SSWG

June 3		Pass 2 changes due to ESPTO

June 10-12	SSWG meeting at ESPTO office to finalize cases

July 1		Cases posted on the ERCOT web site by ESPTO

2.2 DATA SET B CONSIDERATIONS

    - Data Set Uses

Data Set B cases are generally used by TSPs to perform long-range planning studies.

    - Data Set B Case Definitions

ERCOT DATA SET B BASECASES

(YR) = FOLLOWING YEAR

| BASE CASE | # NOTES | TRANSMISSION IN-SERVICE DATE |
| --- | --- | --- |
| (YR+1)SUM1 | 1 | JULY 1, (YR+1) |
| (YR+2)SUM1 | 1 | JULY 1, (YR+2) |
| (YR+3)WIN1 | 1 | JANUARY 1, (YR+3) |
| (YR+3)MIN | 2 | JANUARY 1, (YR+3) |
| (YR+3)SUM1 | 1 | JULY 1, (YR+3) |
| (YR+4)SUM1 | 1 | JULY 1, (YR+4) |
| (YR+5)SUM1 | 1 | JULY 1, (YR+5) |

## Notes

- Cases to represent the maximum expected load during the season.

- Cases to represent the absolute minimum load expected for (YR+3).

    - ERCOT Data Dictionary

With Data Set B, each SSWG member will submit a data file listing all buses that exist in any case from either Data Set A or B.  This file is called the ERCOT Data Dictionary.   The data dictionary is used by ESPTO to show correlation between base case bus numbers and control area ? SCADA names.  Also, the data dictionary without the SCADA names is included as part of ERCOT’s FERC 715 filing.  The format will be as follows:

| Field | Columns | Special Instructions |
| --- | --- | --- |
| Submitter Name | A | TSP |
| Bus Number | B | From load-flow cases |
| Bus Name (as in case) | C | From load-flow cases |
| Base kV of Bus | D | From load-flow cases |
| Full Bus Name | E | Unabbreviated name |
| County where bus located | F | Do not include the word “County” |
| Load Company Name | G | Load description (optional) |
| SCADA Station Names | H | ERCOT ICCP Data link names |

There are several naming conventions that should not be used because it creates problems when the data dictionary is used for ESPTO’s operations load-flow model. The following special characters should not be used: $,%, :, !, @, &, (, ) or ’. No field should begin with an underscore or a # sign. SCADA names should be a maximum of eight characters long, and there should be no duplicate SCADA names at the same voltage level in the ERCOT Data Dictionary. SCADA names are not required for future substations.

    - Schedule

ESPTO shall post all data and information. As an example:

September 10	NOIEs send generation dispatch data to ESPTO

September 17	Raw data files due to ESPTO

September 25	Pass 1 cases due to SSWG

September 30	SSWG general meeting if needed

October 7 	Pass 1 changes due to ESPTO

October 14	Pass 2 cases due to SSWG

October 21	Pass 2 changes due to ESPTO

November 4-6 SSWG meeting at ESPTO office to finalize cases

November 15	Cases posted on the ERCOT web site by ESPTO

2.3 ERROR SCREENING AND CASE UPDATES

SSWG members are responsible for assembling all of the information for the sub-systems they are responsible for and, through a systematic process, creating the load-flow base cases.  This requires many steps, each of which may introduce errors.  To minimize the potential for errors in the cases, there are many data screens and error checks that should be employed.  These can be local or global in nature.

The creation of the load-flow base cases consists of two distinct phases; and, therefore, the screening for and correction of errors will be divided into two different processes.  These two phases are:

- Producing the application for load serving entities’ Annual Load Data Request

- Creating the cases for Data Set A and Data Set B

    - Review of ALDR

The ALDR provides the detailed load data for each customer that is requesting transmission service.  Because of the vastness of the data in the ALDRs, it is critical that they be reviewed and screened with the utmost diligence before their submittal to ESPTO.

- Load shall be consistent with ALDR.

- Load serving entities’ total load plus losses in cases shall be consistent with coincident system load in the ALDR, excluding self-serve load.

- Bus numbers should be within TSP designated SSWG bus range

After ESPTO reviews each ALDR, they are sent to all SSWG members who should review them closely before they are used to create load-flow case data. If ALDR problems are found, SSWG members should contact the entities submitting the data.  Proper communication between TSP should minimize these problems.  Some checks that should be performed (by spreadsheet format) include but are not limited to the following:

- The bus number in column D must be included. No duplicate IDs or bus numbers.

- The coincidence factors in columns K and Q must be less than or equal to 100%.

- The Minimum/Peak value in column T must be less than or equal to 100%.

- All power factors must be less than or equal to 1.

- There should be a continuity of power factors for loads that have changed from one TSP to another.

- The county name should be spelled correctly.

- NA, N/A, or other alphabetic characters should not appear in a numerical field (leave field blank if not sure). Also #DIV/0! and #VALUE! should be deleted.

- There should be only one voltage level for each delivery point.

- In some places the workbook asks for kW or kWH and in some places MW or MWH.  The values must be in the correct measure.

- The calculated diversity factor in row 33 should be greater than or equal to 100%.

- Correct TSP code.

- No missing loads (i.e. loads that have changed from one TSP to another have not been dropped.)

- No duplicate loads.

    - Review of Load-Flow Base Case Data

Checks should include but are not limited to the following:

- Bus numbers should be within that TSP’s designated SSWG bus range

- Zone numbers should be within that TSP’s designated SSWG zone range

- No disconnected buses and swingless islands.

- No buses with blank nominal voltage.

- No radial distribution buses.

- No transformers serving non-network distribution buses.

- Should not be any topology differences between on-peak seasonal cases and corresponding off-peak seasonal cases (e.g. 98SPG1 vs. 98SPG2)

- Branch data checks:

- Every non-transformer branch should have mileage

- Mileage comparison to impedance is reasonable

- Percentage ownerships total 100% for all lines

- No inordinately small impedances (less than 0.0001 p.u.)

- No inordinately large impedance (greater than 3.000 p.u.)

- No inordinately high R/X ratios (absolute value of R greater than 2.0 times absolute value of X)

- Generally no negative reactances (with the exception of 3 winding transformers)

- No inordinately high charging (greater than 5.000 or negative)

- No inordinately high tap ratios (greater than 1.200)

- No inordinately low tap ratios (less than 0.800)

- Zero impedance branches connected to generation buses

- Zero impedance loops (X<0.0001 p.u. on 100 MVA base).  Cases will not solve with mismatches within the zero impedance loops.

- Transformer data checks:

- No transformer RMAX < RMIN

- No transformer VMAX < VMIN

- Difference between VMAX and VMIN should be 0.0125 or greater

- No non-transformer branches between voltages levels

- Generator data checks:

-	No zero generator source impedance (CONG)

-	No maximum generation (PMAX) less than minimum generation (PMIN).

-	No maximum reactive generation (QMAX) less than minimum reactive generation (QMIN).

-	Offline generators should be Type 2 with status 0.

-	No plant specified as remotely regulating itself (remote bus must be zero if self-regulating).

    - Solved Case Checks

A case is considered solved when a power-flow program reaches a solution using the following method:  a Fully Coupled Newton-Rhapson iterative algorithm with transformer tap stepping enabled and tolerance of the largest bus mismatch of .5 MW or MVAR on a 100 MVA base (.005 per unit) or less.  Other solution techniques may be applied prior to executing this solution method to converge the case.

A case shall also meet the following conditions:

- Solve in less than 20 iterations (preferably in less than 12 iterations)

- Switched shunts locked

- Phase shifters enabled

- DC transformer tap stepping enabled

- Generator var limits enforced immediately

- The system swing generation real output should be within the normal operating parameters of the unit.

- Line and equipment loading shall be within applicable thermal rating limits

- No branches loaded above any of Rate A, Rate B or Rate C

- No emergency ratings (Rate B) of branches less than the normal ratings (Rate A).

- Voltage levels shall be maintained within applicable limits

- Voltage control conflicts (for example, PTI’s CNTB ALL)

- Generally no buses with solved voltage above 1.050 p.u.

- Generally no buses with solved voltage below 0.950 p.u.

- ESPTO will run contingency analysis before posting each data set.

# Before finalizing cases each TSP will verify and acknowledge error checking output produced by ESPTO

    - Review of Tie-Line Listing

Coordination between TSPs is critical in maintaining the tie-line listing. Some potential problems that need to be reviewed include:

- Correct add/remove years

- Correct from/to bus numbers

- Correct metering location

- Correct conductor description

- Correct ownership

- Correct mileage and impedance/rating

- TSPs should agree on all ratings

Once the discrepancies are identified, TSPs need to correct the differences and make appropriate updates both to load-flow cases and the tie-line listing.

    - Case Updates

When necessary the TSP will document updates which will be posted by ESPTO. The file name should have a clear description, which will include provider’s acronym and the specific case to be updated.

SECTION 3.0 – Other SSWG Activities

3.1 TRANSMISSION LOSS FACTOR CALCULATIONS

(To be developed later by ESPTO)

3.2 VOLTAGE CONTROL AND REACTIVE PLANNING

(To be determined)

APPENDICES

Appendix A

Owner ID,TSP, Bus/Zone Range Table

|  |  | TSP | ABBREVIATION | TRAN OWNER ID | TSP | PSSE AREA NO. | BUS ALLOCATED | ZONE RANGE |  | ZONE ALLOCATED |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| BUS RANGE |  |  |  |  |  |  |  |  |  |  |
| 1 | 999 | BRAZOS ELECTRIC POWER COOP. | BEPC | 101 | TMPPA | 11 | 1000 | 1 | 99 | 100 |
| 1 | 999 | BRYAN, CITY OF | BRYN | 102 | TMPPA | 11 |  | 1 | 99 |  |
| 1 | 999 | DENTON MUNICIPAL UTILITIES, CITY OF | CODX | 108 | TMPPA | 11 |  | 1 | 99 |  |
| 1 | 999 | GARLAND, CITY OF | COGX | 110 | TMPPA | 11 |  | 1 | 99 |  |
| 1 | 999 | GREENVILLE ELECTRIC UTILITY SYSTEM | GEUS | 113 | TMPPA | 11 |  | 1 | 99 |  |
| 1 | 999 | TEXAS MUNICIPAL POWER AGENCY | TMPA | 127 | TMPPA | 11 |  | 1 | 99 |  |
| 1000 | 3699 | COLLEGE STATON, CITY OF | COCS | 104 | TUETA | 1 |  | 100 | 199 |  |
| 1000 | 3699 | TU ELECTRIC | TUET | 130 | TUETA | 1 | 2700 | 100 | 199 | 100 |
| 3700 | 3999 | TEXAS NEW MEXICO POWER CO. | TNMP | 128 | TMMPA | 17 | 300 | 220 | 249 | 30 |
| 4000 | 4999 | HOUSTON LIGHTING & POWER | HLPT | 114 | HLPTA | 4 | 1000 | 260 | 319 | 60 |
| 5000 | 5499 | CITY PUBLIC SERVICE SAN ANTONIO | CPST | 107 | CPSTA | 5 | 500 | 340 | 369 | 30 |
| 5500 | 5899 | MEDINA ELECTRIC COOP. | MEDX | 111 | STECA | 13 |  | 869 | 898 |  |
| 5500 | 5899 | SOUTH TEXAS ELECTRIC COOP | STEC | 122 | STECA | 13 | 400 | 869 | 898 | 30 |
| 5900 | 5909 | SAN MIGUEL ELECTRIC COOP. | SMEC |  | SMEC | 14 | 10 | 899 | 899 | 1 |
| 5910 | 5919 | SOUTH TEXAS POWER PLANT | STP | 114 | HLPTA | 4 | 10 | 260 | 319 | 60 |
| 5920 | 5929 | EAST HIGH VOLTAGE DC |  |  | AEP | 16 | 10 | 200 | 200 | 1 |
| 5930 | 5989 | PUBLIC UTILITY BOARD OF BROWNSVILLE | PUBX | 119 | PUBXA | 15 | 60 | 800 | 829 | 30 |
| 6000 | 6799 | COLEMAN COUNTY ELECTRIC COOP. | CCEC | 103 | AEP | 8 |  | 402 | 479 |  |
| 6000 | 6799 | CONCHO VALLEY ELECTRIC COOP. | CVEC | 105 | AEP | 8 |  | 402 | 479 |  |
| 6000 | 6799 | MIDWEST ELECTRIC COOP. | MWEC | 118 | AEP | 8 |  | 402 | 479 |  |
| 6000 | 6799 | RIO GRANDE ELECTRIC COOP. | RGEC | 120 | AEP | 8 |  | 402 | 479 |  |
| 6000 | 6799 | SOUTHWEST TEXAS ELECTRIC COOP. | SWTE | 123 | AEP | 8 |  | 402 | 479 |  |
| 6000 | 6799 | STAMFORD ELECTRIC COOP. | SECX | 124 | AEP | 8 |  | 402 | 479 |  |
| 6000 | 6799 | TAYLOR ELECTRIC COOP. | TECX | 125 | AEP | 8 |  | 402 | 479 |  |
| 6000 | 6799 | TEX-LA ELECTRIC COOP | TXLA | 130 | TUETA | 3 |  | 177 | 177 | 1 |
| 6000 | 6799 | WEST TEXAS UTILITIES COMPANY | WTUC | 131 | AEP | 8 | 800 | 402 | 479 | 78 |
| 6096 | 6096 | NORTH HIGH VOLTAGE DC |  |  | AEP | 8 |  | 402 | 479 |  |
| 6800 | 6942 | RAYBURN COUNTRY ELECTRIC COOP | RCEC | 130 | TUETA | 2 | 142 | 178 | 178 | 1 |
| 6800 | 6810 | GRAYSON COUNTY ELECTRIC COOP. | GCEC | 130 | TUETA | 2 | 11 | 178 | 178 | 1 |
| 6811 | 6849 | LAMAR COUNTY ELECTRIC COOPERATIVE | LCEC | 130 | TUETA | 2 | 39 | 178 | 178 | 1 |
| 6850 | 6889 | FARMERS ELECTRIC COOP. | FECX | 130 | TUETA | 2 | 40 | 178 | 178 | 1 |
| 6890 | 6899 | TRINITY VALLEY ELECTRIC COOPERATIVE | TVEC | 130 | TUETA | 2 | 10 | 178 | 178 |  |
| 7000 | 7899 | LOWER COLORADO RIVER AUTHORITY | LCRA | 116 | LCRAA | 7 | 900 | 500 | 589 | 90 |
| 7000 | 7899 | SOUTHWESTERN ELECTRIC SERVICE CO. | SESC | 121 | LCRAA | 7 |  | 100 | 199 |  |
| 8000 | 8999 | CENTRAL POWER & LIGHT COMPANY | CPLC | 106 | AEP | 8 | 1000 | 610 | 669 | 60 |
| 8000 | 8999 | MAGIC VALLEY ELECTRIC COOP. | MVEC | 117 | AEP | 8 |  | 654 | 655 | 2 |
| 9000 | 9399 | AUSTIN ENERGY | AENX | 100 | AENXA | 9 | 400 | 690 | 719 | 30 |
| 9400 | 9999 | ERCOT SYSTEM PLANNING | ESPTO | XXX | ESPTO | XXX | XXX | 900 | 999 | 100 |
| 10000 | 31999 | TU ELECTRIC | TUET | 130 | TUETA | 1 | 22000 | 100 | 199 | 100 |
| 10000 | 31999 | COLLEGE STATON, CITY OF | COCS | 104 | TUETA | 1 |  | 100 | 199 |  |
| 32000 | 36999 | BRAZOS ELECTRIC POWER COOP. | BEPC | 101 | TMPPA | 11 | 5000 | 1 | 99 | 100 |
| 32000 | 36999 | BRYAN, CITY OF | BRYN | 102 | TMPPA | 11 |  | 1 | 99 |  |
| 32000 | 36999 | DENTON MUNICIPAL UTILITIES, CITY OF | CODX | 108 | TMPPA | 11 |  | 1 | 99 |  |
| 32000 | 36999 | GARLAND, CITY OF | COGX | 110 | TMPPA | 11 |  | 1 | 99 |  |
| 32000 | 36999 | GREENVILLE ELECTRIC UTILITY SYSTEM | GEUS | 113 | TMPPA | 11 |  | 1 | 99 |  |
| 32000 | 36999 | TEXAS MUNICIPAL POWER AGENCY | TMPA | 127 | TMPPA | 11 |  | 1 | 99 |  |
| 37000 | 39999 | TEXAS NEW MEXICO POWER CO. | TNMP | 128 | TMMPA | 17 | 3000 | 220 | 249 | 30 |
| 40000 | 49999 | HOUSTON LIGHTING & POWER | HLPT | 114 | HLPTA | 4 | 10000 | 260 | 319 | 60 |
| 50000 | 54999 | CITY PUBLIC SERVICE SAN ANTONIO | CPST | 107 | CPSTA | 5 | 5000 | 340 | 369 | 30 |
| 55000 | 58999 | MEDINA ELECTRIC COOP. | MEDX | 111 | STECA | 13 |  | 869 | 898 |  |
| 55000 | 58999 | SOUTH TEXAS ELECTRIC COOP | STEC | 122 | STECA | 13 | 4000 | 869 | 898 | 30 |
| 59000 | 59099 | SAN MIGUEL ELECTRIC COOP. | SMEC |  | SMEC | 14 | 100 | 899 | 899 | 1 |
| 59100 | 59199 | SOUTH TEXAS POWER PLANT | STP | 114 | HLPTA | 10 | 100 | 260 | 319 | 60 |
| 59200 | 59299 | EAST HIGH VOLTAGE DC |  |  | AEP | 16 | 100 | 200 | 200 | 1 |
| 59300 | 59899 | PUBLIC UTILITY BOARD OF BROWNSVILLE | PUBX | 119 | PUBXA | 15 | 600 | 800 | 829 | 30 |
| 60000 | 67999 | COLEMAN COUNTY ELECTRIC COOP. | CCEC | 103 | AEP | 8 |  | 402 | 479 |  |
| 60000 | 67999 | CONCHO VALLEY ELECTRIC COOP. | CVEC | 105 | AEP | 8 |  | 402 | 479 |  |
| 60000 | 67999 | MIDWEST ELECTRIC COOP. | MWEC | 118 | AEP | 8 |  | 402 | 479 |  |
| 60000 | 67999 | RIO GRANDE ELECTRIC COOP. | RGEC | 120 | AEP | 8 |  | 402 | 479 |  |
| 60000 | 67999 | SOUTHWEST TEXAS ELECTRIC COOP. | SWTE | 123 | AEP | 8 |  | 402 | 479 |  |
| 60000 | 67999 | STAMFORD ELECTRIC COOP. | SECX | 124 | AEP | 8 |  | 402 | 479 |  |
| 60000 | 67999 | TAYLOR ELECTRIC COOP. | TECX | 125 | AEP | 8 |  | 402 | 479 |  |
| 60000 | 67999 | TEX-LA ELECTRIC COOP | TXLA | 126 | TUETA | 3 |  | 177 | 177 | 1 |
| 60000 | 67999 | WEST TEXAS UTILITIES COMPANY | WTUC | 131 | AEP | 8 | 8000 | 402 | 479 | 78 |
| 68000 | 68109 | GRAYSON COUNTY ELECTRIC COOP. | GCEC | 112 | TUETA | 2 | 110 | 178 | 178 | 1 |
| 68110 | 68499 | LAMAR COUNTY ELECTRIC COOPERATIVE | LCEC | 115 | TUETA | 2 | 390 | 178 | 178 | 1 |
| 68500 | 68899 | FARMERS ELECTRIC COOP. | FECX | 109 | TUETA | 2 | 400 | 178 | 178 | 1 |
| 68900 | 68999 | TRINITY VALLEY ELECTRIC COOPERATIVE | TVEC | 129 | TUETA | 2 | 100 | 178 | 178 | 1 |
| 70000 | 78999 | LOWER COLORADO RIVER AUTHORITY | LCRA | 116 | LCRAA | 7 | 9000 | 500 | 589 | 90 |
| 70000 | 78999 | SOUTHWESTERN ELECTRIC SERVICE CO. | SESC | 121 | LCRAA | 7 |  | 100 | 199 |  |
| 80000 | 89999 | CENTRAL POWER & LIGHT COMPANY | CPLC | 106 | AEP | 8 | 10000 | 610 | 669 | 60 |
| 80000 | 89999 | MAGIC VALLEY ELECTRIC COOP. | MVEC | 117 | AEP | 8 |  | 654 | 655 | 2 |
| 90000 | 93999 | AUSTIN ENERGY | AENX | 100 | AENXA | 9 | 4000 | 690 | 719 | 30 |
| 94000 | 99997 | RESERVED FOR FUTURE USE | ESPTO | XXX | ESPTO | XXX | 3998 | 900 | 999 | 100 |

Appendix B

Glossary of Terms

ALDR – Annual Load Data Request

BUS– A node representing point of electrical connection, such as substation or radial tap point.

ERCOT – Electric Reliability Council of Texas

ESPTO – ERCOT System Planning

IPP  – Independent power producer

LSE – Load serving entity

LTC – Load tap changing transformer

MLSE – Most limiting series element

MSL – Multi-section line

NERC – North American Electric Reliability Council

NESC – National Electric Safety Code

NOIE – Non-opt-in Entity

NUG – Non Utility Generator

PUCT – Public Utility Commission of Texas

QSE – Qualified Scheduling Entity

REP – Retail Electric Provider

SSWG – Steady State Working Group

TSP – Transmission Service Provider

VCRP – Voltage control and reactive planning

Zone – A predefined sub-system within a load-flow case.

Appendix C

TSP Impedance and Line Ratings Assumptions

Reliant Energy HL&P

Reliant Energy uses the Line Constants (LC) module of the Computer Aided Protection Engineering (CAPE) which is a software developed and supported by Electrocon International Incorporated.  LC calculates the line constant parameters for overhead transmission lines.  LC calculates the total self-series positive and zero sequence impedance and self-shunt positive and zero sequence admittance of the main circuit in a given right-of-way section.  LC also calculates the total mutual zero sequence series impedance and shunt admittance between the main circuit and all other circuits in the given right-of-way section.

LC does not calculate impedance for underground cables.  Instead per-mile impedance data provided by the manufacturer is entered in parameter codes.  LC multiplies this per-mile impedance with the actual mileage of the circuit to calculate total impedance for the underground cable.

Data used (conductor catalog, tower design, soil resistivity, parameter codes, right-of-way data, tower string data, line data and line section data) in LC calculation is stored in a database called TLIP.gdb.  Calculated parameters are also stored in a TLIP database.

Line Constants

Assumptions used in the calculations are:

- Earth resistivity = 10 ohm-meters.

- Frequency = 60 Hz.

- Conductor characteristic data from T&D Reference Book, Aluminum Electrical Conductor Handbook Second Edition 1982 from the Aluminum Association.

- Conductor temperatures used for calculating impedance: 25oC.

- Ground wires are included in zero sequence impedance calculations.

- Actual tower and pole configurations are used in calculations.

- Actual length of line is used.

- Sag characteristics are based upon the type of structure being studied.

Transformer Constants

Transformer impedance is calculated when possible using data from the manufacturer’s test reports and industry accepted formulas to convert the manufacturer's test results data to resistance and reactance values on the required per-unit base.  If it is not available, HL&P will use typical data from similar transformers in the system

Assumptions used in the calculations are:

- Frequency = 60 Hz.

- Temperatures vary depending upon the vendor test data.

Conductor Ratings

Conductor ampere ratings are calculated by the IEEE method detailed in ANSI/IEEE Standard 738-93 with the following input parameters:

Latitude  = 28 N

Wind Velocity  = 3 feet per second

Wind Angle = 30° to conductor

Emissivity Coefficient  = 0.5

Solar Absorption Coefficient  = 0.5

Line Elevation  = 500 feet AMSL

Line Orientation  = East – West

Time of Day   = 2 P.M.

Atmospheric Condition  = Clear

Air Temperature  = 36 C

The normal rating is the maximum current carrying capacity of an element for continuous operation without causing any loss of life.  For overhead transmission conductor this capacity is the ampacity of the conductor at 75oC unless the conductor has enough clearance for operating continuously at 90oC The normal rating for switches, breakers, transformers, current transformers, wave traps etc. is the maximum nameplate rating.

The emergency rating is the maximum current carrying capacity of an element for a short duration with acceptable loss of life. For overhead transmission conductor it is the ampacity of the conductor at 90oC unless the conductor has been surveyed and cleared for operating at a higher temperature for a short duration. For underground transmission conductor the emergency rating is the maximum allowable ampacity for 300 hours of emergency operation.  For substation facilities such as switches, breakers, transformers, current transformers etc. the emergency rating is the same as the normal rating.

The emergency rating of the conductor is the conductor thermal rating.

Line Ratings

The maximum overall rating of a transmission line is the current carrying capability of the most limiting element in series between the breakers at its two end points.  Unless otherwise limited by equipment ratings installed in the transmission line circuit such as breakers, current transformers, switches, disconnects, wave traps, jumpers, the normal and emergency rating of a transmission line is the conductor normal and emergency ratings.  Where such equipment has a manufacturer's nameplate continuous current rating less than the conductor normal and/or emergency rating, then that equipment’s continuous rating shall be used for the normal and/or emergency rating of the transmission line.

Transformer Ratings

The normal and emergency rating of a transformer is the manufacturer’s test data’s highest continuous FA or FOA rating at 65C rise, depending upon the particular transformer.

# Texas-New Mexico Power Company

Conductor Ratings

Conductor thermal ratings are calculated by the IEEE method detailed in ANSI/IEEE Standard 738 with the following input parameters:

Latitude  = 30 N

Wind Velocity  = 2 feet per second

Wind Angle = 90° to conductor

Emissivity Coefficient  = 0.5

Solar Absorption Coefficient  = 0.5

Line Elevation  = 600 feet AMSL

Line Orientation  = East – West

Time of Day   = 2 P.M.

Atmospheric Condition  = Clear

Air Temperature  = 25 C

Conductor Temperature  = 75 C

The emergency rating of the conductor is the conductor thermal rating.  The normal rating is 90% of the conductor thermal rating. No allowance is made for design or operational thermal limits such as conductor sag or for circuit elements other than the transmission line conductor.

Line Ratings

Unless otherwise limited by equipment ratings installed in the transmission line circuit such as breakers, current transformers, switches, disconnects, wave traps, jumpers, the normal and emergency rating of a transmission line is the conductor normal and emergency ratings. Where such equipment has a manufacturer's continuous current rating less than the conductor normal and/or emergency rating, then that equipment continuous rating shall be used for the normal and/or emergency rating of the transmission line.

Transformer Ratings

The normal rating of a transformer is the manufacturer’s highest continuous FA rating at 55C rise.

The emergency rating of a transformer is the manufacturer’s highest continuous FA rating at 65C rise.

Line Constants

Line impedance constants are calculated in a TNMP developed Transmission Line Impedance Calculation spreadsheet using formulas detailed in the Electrical Transmission and Distribution Reference Book by Westinghouse (T&D Reference Book).  Factors used in the calculations are:

- Conductor characteristic data from T&D Reference Book, Electrical Conductor Handbook, or manufacturer's data sheets

- Tower or pole and conductor configuration information

- Actual length of line with no allowance for sag

- Earth resistivity = 100 ohm-meters

- Frequency = 60 Hz

- Ground wires are included in zero sequence impedance calculations

Transformer Constants

Transformer impedance is calculated using data from the manufacturer’s test reports and industry accepted formulas to convert the manufacturer's test results data to resistance and reactance values on the required per-unit base.

City Public Service

Line constants

City Public Service uses a modified version of Green and Bowen's

"Calculation of Series Shunt Line Constants" program.  The modified version

of this program takes input data describing one or more transmission lines on a common right of way and calculates self and mutual line constants

required for load-flow and fault current studies.

Assumptions used to make calculations:

Earth resistivity is 100 ohm-meters.

Frequency is 60 Hz.

The conductor names follow the convention, 1272AA(AWG or

kcmil size, and stranding class), as described in the Aluminum Association

Electrical Conductor Handbook Third Edition 1989.

Conductor temperature used for calculating impedance: 50oC.

Typical conductor data: resistance, reactance, size of conductor, used in the calculations.

Data comes from Aluminum Association Electrical Conductor Handbook Third Edition 1989 or Electrical T&D Reference Book Westinghouse Electric Corporation Fourth Edition Copyright 1964.

Ground wires are included.  Use diameter, resistance, and reactance in ohms/mile.

Actual tower configurations are used.

Actual line lengths are used.

Conductor sag is included in the calculation using typical data.

Transformer constants

Impedance is calculated.

In order to calculate transformer impedance,  test report results are ratioed to required parameters.

Assumptions used to make calculations:

Transformer test reports.

Earth resistivity is 100 ohm-meters.

Frequency is 60 Hz.

Temperature used for calculating impedance: 85oC.

Typical transformer data: resistance, reactance used in the calculations.

Data comes from transformer test reports

Ratings Calculation

Lines - Branches

Ratings are calculated from a program that uses the IEEE Standard for Calculation of Bare Overhead Conductor.  Conductor characteristics are taken from the Aluminum Association Electrical Conductor Handbook.

Conductor temperature used for emergency and normal for these ratings. 75oC.

Loading levels are tolerated until 100% of rating.  Begin taking action at 90% of rating.

Assumptions used to make normal and emergency calculations:

Normal line ratings are calculated using 25o ambient temperature.

75oC conductor temperature.

1.4 mph wind.

Solar emissivity of .5.

Solar absorption = 0.5.

Wind direction S-N or E-W, choice in program.

Elevation is 600 ft above sea level.

Latitude is 30o.

The level of wave trap loading is selected specifically for line rated higher than conductor.

Current transformers are loaded to CT rating multiplied by thermal rating factor.

Switches are loaded to manufacturer's rating.

If these rates are lower than conductor rating, they are the emergency rating for that circuit.

Transformers - branches

Normal transformer ratings are calculated by using the manufacturer’s highest rating either 55oC  or 65 o C,  highest FA or FOA rating.

Basis for rating for transformers is transformer test reports.

What temperature is your emergency and normal used for these ratings?

The emergency and normal temperature used for these ratings is the highest transformer test report rating temperature.

These loading levels are tolerated until reaching 100%, then take immediate action, prepare for action at 90%

Assumptions used in making normal and emergency calculation are completely from manufacturer's test reports

Emergency transformer ratings are same as normal ratings

This rating is the only rating used for studies concerning transformers

No other ratings are used for studies.

Lower Colorado River Authority

Line Constants

The LCRA utilizes a database to keep tabulated data and perform calculations for positive and zero sequence values (R, X, Ro, Xo) and charging values (B).  These calculations and some tabulated values are used for input in a load-flow modeling software (PSS/E).  Standard formulas are used and can be found in the Westinghouse Electrical Transmission & Distribution Reference Book or other similar textbooks.

The following assumptions are made in the calculations:

Earth resistivity is 100 meters

Frequency is 60 Hz

The conductor names follow the standard convention, such as Drake & Penguin

Typical data (resistance, reactance) from “Southwire Company Overhead Conductor Manual”

Conductor temperature used for calculating impedance: 50°C

Conductor length based on Surveyed Horizontal Plane Distances

Standard Voltage (69kV, 138kV, 345kV, etc.)

Actual tower configurations provide values of conductor, bundling, and ground wire spacing

Mutual effects from parallel circuits are not included as of this time

Ampacity is based on maximum conductor sag allowed based on NESC clearance requirements.  Currently all new circuits are designed for a sag at 200°F.  However, a few circuits in LCRA’s system are limited to a maximum operating temperature lower than 200°F based on clearance requirements.

Ampacity calculations are performed by using the IEEE Standard for Calculating the Current-Temperature Relationship of Bare Overhead Conductors (IEEE Std 738-1993).   There are currently two environmental conditions with different assumptions.  Environ_Cond 2 represents one high altitude circuit and Environ_Cond 1 represents all other circuits in the system.  The following are the assumptions:

| ENVIRON_COND | Elevation (ft) | Azimuth Line | Line Latitude | Time (Military) | ## Ambient Temp. F° | Wind Velocity | Emissivity | Solar absorptivity | ## Atmosphere |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 600 | 0 | 30 | 14 | 105 | 2 | 0.5 | 0.5 | CLEAR |
| 2 | 5000 | 90 | 30 | 14 | 105 | 2 | 0.5 | 0.5 | CLEAR |

# Conductor Rating

Planned transmission line loading will be such that National Electrical Safety Code line-to-ground clearances will be maintained for all anticipated normal and contingency conditions. Transmission system power flow shall not exceed 100% of the conductor thermal rating.  Full conductor thermal ratings are assigned as shown in the table below.  The conductor ratings are based upon a 93.33 C (200 F) average conductor temperature using coefficients of emissivity and absorptivity of 0.5, a 40.55o C (105 o F) ambient temperature, an elevation of 600 feet above sea level, north-south line orientation, 30 o latitude, 2:00 PM solar conditions, clear atmosphere, and a wind velocity of 2 feet per second normal to the conductor.

TYPICAL CONDUCTOR THERMAL RATINGS

| Conductor Size | Conductor Ampacity | MVA Rating (69 kV) | MVA Rating (138 kV) | MVA Rating (345 kV) |
| --- | --- | --- | --- | --- |
| 1/O ACSR | 256 | 31 | not used | not used |
| 4/O ACSR | 396 | 47 | 95 | not used |
| 336 ACSR | 534 | 64 | 128 | not used |
| 336x2 ACSR | 1068 | 128 | 255 | not used |
| 477 ACSR | 666 | 81 | 159 | not used |
| 795 ACSR | 920 | 110 | 220 | not used |
| 795x2 ACSR | 1840 | 220 | 440 | 1099 |
| 1192.5 ACSR | 1168 | 140 | 279 | not used |

Auto-transformer Rating

Planned loading on auto-transformers, during normal, single, or multiple contingency conditions, shall be limited to 100% of the auto-transformer’s nameplate 65 C rise megavoltampere (MVA) rating.

Austin Energy

Line Constants

Austin Energy uses PTI’s Transmission Line Characteristics program (TMLC) to calculate the line constants. TMLC accepts input data either interactively or from an ASCII text file. The program requires (1) conductor sag and tower configuration data, (2) conductor characteristic data, (3) the phase location on the tower.

Assumptions used to make the line constant calculations:

Earth resistivity is 100 ohm-meters.

#### Frequency is 60 Hz

The conductor names follow the standard convention such as Drake, Rail or Puffin, as described in the Aluminum Association Electrical Conductor Handbook.

#### Conductor temperature used for calculating impedance: 75C

Typical conductor data used:

Resistance (Rac and Rdc), inductive reactance, capacitive reactance and conductor rating.

Data comes from the Electrical Conductor Handbook and Electrical T&D Reference Book.

The calculation includes ground wires in the calculations.

The actual tower configuration is used in the calculations.

The actual length of line is used in the calculations.

The conductor sag is included in calculation and it is determined graphically.

Transformer Constants Austin Energy uses either the transformer test report data or the manufacturer specification sheets data.

Assumptions used to make the calculations:

### Frequency is 60 Hz

Temperature used for calculating impedance: 75-85C

### Typical transformer data: resistance, reactance are used in the calculations

Data comes from transformer test reports

Ratings Calculation

Line Branches

Austin Energy utilizes the ampacity table developed by the BICC Utility Cable Company for the transmission line ratings. For the equipment at the substation termination, Austin Energy uses the nameplate ratings for the circuit breakers and the new re-rated ratings for other equipment such as switches, jumpers, and wave traps.

Assumptions used for normal and emergency ratings.

# For ACSR conductors: Emergency rating at 100C, normal rating set at 90% of emergency rating.

For ACSS conductors: Emergency rating at 200C, normal rating set at 90% of emergency rating.

Normal line ratings are calculated using 40C ambient temperature.

Wind speed = 2 feet/second with sun.

Frequency of operation = 60 Hz.

Solar absorption/emissivity = 0.5

Wave traps, current transformers and load switches can be loaded to the normal rating under normal conditions and can be loaded to the emergency rating under contingency conditions.

The normal rating of the most limiting series element (Rate A) is applied under normal condition, and the emergency rating of the most limiting series element (Rate B) is applied under contingency condition.

## Transformers Branches

Emergency transformer rating is specified as 100% of manufacturer’s nameplate FA or FOA rating at 65C rise, at an ambient temperature of 20C.  Normal transformer ratings are specified as 90% of the emergency transformer rating.

The normal and emergency ratings are good forever.

The newer 345/138 kV auto-transformers have FA ratings.

The older auto-transformers have FOA ratings.

Under normal conditions, the loading of the transmission lines and transformers should be less than the normal ratings, while under contingencies, the loading has to be 100% or less of the emergency ratings.  If the loading exceeds the ratings, operational fixes or transmission additions are considered.

South Texas Electric Cooperative, Inc.

Line constants

Standard formulas are used and can be found in the Westinghouse Electrical Transmission and Distribution Reference Book or other similar textbooks to perform calculations for positive and zero sequence values (R, X, Ro, Xo) and charging values (B).  These calculations and some tabulated values are used for input in a load-flow modeling software (PSS/E).

The following assumptions are made in the calculations:

Earth resistivity is 100 -meters

Frequency is 60 Hz

The conductor names follow the standard convention, such as Drake & Penguin

Typical data (resistance, reactance) from “Southwire Company Overhead Conductor Manual”

Conductor temperature used for calculating impedance: 50°C

Conductor length based on Surveyed Horizontal Plane Distances

Standard Voltage (69kV, 138kV, 345kV, etc.)

Actual tower configurations provide values of conductor, bundling, and ground wire spacing

Ampacity is based on maximum conductor sag allowed based on NESC clearance requirements.  Currently all new circuits are designed for a sag at 167°F.  However, several existing circuits in STEC’s transmission system are limited to a maximum operating temperature lower than 167°F due to limiting elements.

Ampacity calculations are performed by using the IEEE Standard for Calculating the Current-Temperature Relationship of Bare Overhead Conductors (IEEE Std 738-1993).

Conductor Ratings  This should not be underlined, but I couldn’t remove the underline.

Planned transmission line loading will be such that National Electrical Safety Code line-to-ground clearances will be maintained for all anticipated normal and contingency conditions. Transmission system power flow shall not exceed 100% of the conductor thermal rating.  Full conductor thermal ratings are assigned as shown in the table below.  The conductor ratings are based upon 167º F average conductor temperature using coefficients of emissivity and absorptivity of 0.4, a 40.55o C (105o F) ambient temperature, an elevation of 100 feet above sea level, east-west line orientation, 28o latitude, 2:00 PM solar conditions, clear atmosphere, and a wind velocity of 2 feet per second normal to the conductor.

TYPICAL CONDUCTOR THERMAL RATINGS

| CONDUCTOR RATING CONDUCTOR RATING IN MVA 2-CONDUCTOR |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CONDUCTOR IN AMPS 69 kV 138 kV 345 kV BUNDLE |  |  |  |  |  |  |  |  |  |
| SIZE | NORM | EMERG | NORM | EMERG | NORM | EMERG | NORM | EMERG | 345kV |
| 1/0 ACSR | 207 | 230 | 25 | 27 | 49 | 55 | 124 | 137 |  |
| 2/0 ACSR | 243 | 270 | 29 | 32 | 58 | 65 | 145 | 161 |  |
| 2/0 CU | 324 | 360 | 39 | 43 | 77 | 86 | 194 | 215 |  |
| 4/0 ACSR | 306 | 340 | 37 | 41 | 73 | 81 | 183 | 203 |  |
| 4/0 CU | 432 | 480 | 52 | 57 | 103 | 115 | 258 | 287 |  |
| 266 ACSR | 414 | 460 | 49 | 55 | 99 | 110 | 247 | 275 |  |
| 366 ACSR | 477 | 530 | 57 | 63 | 114 | 127 | 285 | 317 |  |
| 477 AA | 582 | 647 | 69 | 77 | 139 | 154 | 348 |  |  |
| 477 ACSR | 603 | 670 | 72 | 80 | 144 | 160 | 360 | 400 |  |
| 556 AA | 639 | 710 | 76 | 85 | 153 | 170 | 382 | 424 |  |
| 556 ACSR | 657 | 730 | 79 | 87 | 157 | 174 | 393 | 436 |  |
| 795 AA | 810 | 900 | 97 | 108 | 194 | 215 | 484 | 538 |  |
| 795 ACSR | 810 | 900 | 97 | 108 | 194 | 215 | 484 | 538 | 1080 |
| 1033 AA | 945 | 1050 | 113 | 125 | 226 | 251 | 565 | 627 |  |
| 1033 ACSR | 954 | 1060 | 114 | 127 | 228 | 253 | 570 | 633 | 1270 |
| 1272 AA | 1089 | 1210 | 130 | 145 | 260 | 289 | 651 | 723 | 1430 |
| 1590 AA | 1246 | 1385 | 149 | 166 | 298 | 331 | 745 | 828 |  |
| 1590 ACSR | 1242 | 1380 | 148 | 165 | 297 | 330 | 742 | 825 | 1650 |
| 2000 AA | 1350 | 1500 | 161 | 179 | 323 | 359 | 807 | 896 |  |

The emergency ratings are based on 25o C ambient, 75o  C conductor temperature, 1.4 mph wind, sun.  Normal ratings are 90%of the emergency rating.

Auto-transformer MVA Ratings

1. Normal rating:	Manufacturer’s FOA rating at 55o C rise.

2. Emergency rating:	Manufacturer’s FOA rating at 65o C rise.

Current Transformer Ratings

1.  Normal rating:	90% of manufacturer’s specified rating.

2.  Emergency rating:	100% of manufacturer’s specified rating.

TXU Electric

TXU Electric Line Constants calculation

TXU Electric uses the APSEN Line Constants Program for calculating Line Impedance.  The ASPEN program consists of two modules, the ASPEN Construction module and the Lines Construction module.  The Construction Module contains tower configuration data for each right-of-way in a system.  This data consists of tower spacing, sag, bundle separation (if applicable) and conductor type.  The Lines Construction module is where the point-to-point line section is constructed.  For each line section the mileage data is entered and a tower configuration from the Construction Module is referenced for calculating the impedance.  The TXU Electric system consists of 621 lines (breaker to breaker) with 3373 total sections.  Calculations are performed with the following constants:

Earth resistivity	100 ohms-meter

Frequency		60 Hz

Conductor Temp	50 °C

Ground wires are included in the calculations

Typical sag is assumed for each voltage level.

22.52 feet for 345 kV

13.33 feet for 138 kV

8.92 feet for 69 kV

Conductor data (resistance, reactance, and outside diameter) is taken from the EPRI Transmission Line Reference book.

Transformer Constants

Transformer impedance is calculated when possible using data from the manufacturer’s test reports and industry accepted formulas to convert the manufacturer's test results data to resistance and reactance values on the required per-unit base.  If actual data is not available, typical data from similar transformers in the system is used.

Conductor Ratings

Conductor ampere ratings are calculated by the IEEE method detailed in ANSI/IEEE Standard 738-86 with the following input parameters:

Wind speed: 2 feet per second normal to conductor

Line orientation: North – South

Coefficient of emissivity: 0.5

Coefficient of solar absorption: 0.5

Line elevation above sea level: 600 feet

Local sun time: 2:00 PM.

Ambient temperature: 40°C

Conductor temperature: 90°C

Line latitude: 32° north

Atmospheric conditions: clear

TXU Electric does not use a normal rating for transmission lines.  Normal loadings up to the emergency rating are acceptable on a continuous basis.   Some TXU Electric transmission lines are designed to operate with a conductor temperature greater than 90°C.   Each line is rated using the ambient assumptions defined earlier and the maximum conductor temperature unique to that line.

The short-term emergency rating is the maximum current carrying capacity of the conductor for a short duration with acceptable line clearance.  For overhead transmission conductor it is 110% of the ampacity of the conductor at 90oC if the line has been surveyed and cleared for operating at a higher temperature for a short duration and the nameplate rating of the switches, breakers and current traps is greater than or equal to 110% of the conductor rating.  For underground transmission conductor the emergency rating is 300 hours of emergency operation at 100°C.

Line Ratings

The maximum overall rating of a transmission line is the current carrying capability of the most limiting element in series between the breakers at its two end points.  Unless otherwise limited by equipment installed in the transmission line such as breakers, current transformers, switches, disconnects, wave traps, jumpers, the emergency rating of a transmission line is the conductor emergency rating.  Where such equipment has a manufacturer's nameplate continuous current rating less than the conductor emergency rating, then that equipment’s continuous rating shall be used for the emergency rating of the transmission line.

Transformer Ratings

Both normal and emergency ratings are calculated in accordance with either ANSI/IEEE Standard C57.92 (1981) or IEEE Standard 756-1984.  Both summer and winter ratings are based upon appropriate daily load and ambient temperature cycles.

Normal ratings are based upon no reduction in normally expected transformer life.

Emergency ratings are based upon the occurrence of two or three long-duration (months) or multiple short-duration (days) contingencies affecting the life of a transformer.  They recognize a hottest spot limit to prevent bubble evolution and a limitation in the loss of transformer expected life of no more than 0.2% per daily load cycle.  (Tests indicate that bubble evolution may occur in operating power transformer at temperatures of 140°C and above; however, a maximum emergency hottest spot temperature of 135°C is used for planning purposes to allow for abnormally high daily loads and/or ambient temperatures.)

Limiting temperatures in degrees C are as follows:

Maximum Hottest Spot

Rated Rise	Top Oil	Normal	Emergency

55		   100		   105		     135

65		   110		   120		     135

Summer Ambient – 40o C

# TMPA Line and Equipment Ratings

Transmission Line Conductor        Emergency ratings are based on 25o C ambient, 75o C

conductor temperature,  1.4 mph wind, sun.

Normal ratings are 90% of the emergency rating.

Auto-transformer MVA Ratings

- .   Normal rating:  Manufacturer FOA rating at 55o C rise.

- Emergency rating:  Manufacturer FOA rating at 65 o C rise.

Current Transformer Ratings Normal rating:  90% of manufacturer specified rating.

Emergency rating:  100%  of manufacturer specified rating.

Substation Bus and Equipment Normal Voltage Ratings

69 kV:  65.55 kV – 72.45 kV

- 138 kV:  131.10 kV – 144.9 kV

- 345 kV:  327.75 – 362.25 kV

Oil and Gas Circuit Breaker Current Ratings

- Normal rating:  90% of  manufacturer specified rating.

Emergency rating:  100% of  manufacturer specified rating.

City of Garland

Line Constants

Westinghouse T&D Textbook

Earth resistivity is 100 ohms – meter

Frequency is 60 Hz

3% sag

Manufacturers data:  resistance and reactance per phase per mile

Actual length of lines

Actual tower configurations

Use ground wires

Conductor temperature 50o C

Transformer Constants

Use manufacturer actual nameplate data

### City of Denton

The city of Denton owns only 69kV transmission lines and no transmission voltage transformers.  Little historical information is available to indicate the exact methodology used in developing impedance date for the 69kV lines.  It appears that the data was developed in the early 1980s using the Westinghouse method.  These values were apparently verified, or at least accepted, by TMPA.  The values developed are still in use in analytical programs.  Line impedance data for line construction or line rebuilds will be developed using the ASPEN program.  Evaluation of the potential effect of proposed conductor size changes indicate that the impedance values in use are within reason.  Data for all line sections will be reviewed in the future and documentation prepared to describe methodology.

Line Ratings

The 50 C conductor ratings are used as the normal and the emergency ratings for existing lines.  Almost all transmission lines are underbuilt with one or two distribution circuits.  This limits the amount of sag that can be tolerated.  Specific historical design information is not available to use in evaluating potential ratings.  Studies will be undertaken as needed to determine possible increases in ratings.  New lines will be designed for 100 C operation.

# Brownsville Public Utilities Board

Line Constants Line impedance constants are calculated using formulas detailed in the Electrical Transmission and Distribution Reference Book by Westinghouse (T&D Reference Book).  Factors used in the calculations are:

- Conductor characteristic data from T&D Reference Book, Electrical Conductor Handbook, or manufacturer's data sheets

- Tower or pole and conductor configuration information

- Actual length of line with no allowance for sag

- Earth resistivity = 100 ohm-meters

- Frequency = 60 Hz

- Ground wires are included in zero sequence impedance calculations

Transformer Constants

Transformer impedance is calculated using data from the manufacturer’s test reports and industry accepted formulas to convert the manufacturer’s test results data to resistance and reactance values on the required per-unit base. If it is not available, PUB will use typical data from similar transformers.

Conductor Ratings

Conductor thermal ratings are calculated using the IEEE method detailed in ANSI/IEEE Standard 738 with the following input parameters:

Latitude  = 30 N

Wind velocity  = 2 feet per second

Wind angle = 90° to conductor

Emissivity coefficient  = 0.5

Solar absorption coefficient  = 0.5

Line elevation  = 600 feet AMSL

Line orientation  = East – West

Time of day   = 2 P.M.

Atmospheric condition  = Clear

Air temperature  = 25 C

Conductor temperature  = 75 C

The normal rating is 90% of the conductor thermal rating. The emergency rating of the conductor is the conductor thermal rating. No allowance is made for design or operational thermal limits such as conductor sag or for circuit elements other than the transmission line conductor.

Line Ratings

The maximum overall rating of a transmission line is the current capability of the most limiting element in series between its two end points. Unless otherwise limited by equipment ratings installed in the transmission line circuit such as breakers, current transformers, switches, disconnects, wave traps, jumpers, the normal and emergency rating of a transmission line is the conductor normal and emergency ratings.

Transformer Ratings

The normal rating of a transformer is the manufacturer’s highest continuous FA rating at 55C rise.

The emergency rating of a transformer is the manufacturer’s highest continuous FA rating at 65C rise.

American Electric Power Service Corporation (AEPSC) Line Constants Calculation

Currently American Electric Power Service Corporation (AEPSC)) uses a Transmission Line Constants program (TLC) that was developed by Electric Power Research Institute (EPRI) in 1981 that computes electrical transmission parameters. Inputs to the program are collected from manufacturer’s test reports and data collected from the field and used conjunction with industry accepted methods to calculate the modeling data required in the AEPSC/ERCOT load-flow cases.

AEPSC uses actual transformer test data in calculating the transformer’s impedance. When actual test data is not available, engineering assumptions and nameplate data are employed to determine the impedance that will be used in modeling the transformers in AEPSC/ERCOT load-flow cases.

- Input Data / Assumptions

- Operating Voltages 69kV and above

- Actual structure geometry, tower height, including shield wire

- Resistance and reactance are calculated at 50o C

- Actual conductor length – breaker to breaker

- Conductor characteristics geometric mean radius, conductor radius, resistance, reactance, etc. from

- Electrical Transmission and Distribution Reference Book, prepared by Central Station Engineers of the Westinghouse Electric Corporation

- Transmission Line Reference Book, 345 kV and Above/ Second Edition, prepared by Project UHV Technical Resource Operation Large Transformer Division General Electric Co. Pittsfield, Massachusetts; Transmission Engineering Electric Utility System Engineering Department, Energy Systems and Technology Division General Electric Co., Schenectady, New York and Electric Power Research Institute, Palo Alto, California.

- Manufacturer's provided data is used for the specific conductor's ratings.

- Sag is not included in impedance calculation

- Frequency 60 Hz

- Manufacturer’s transformer test reports

- Earth resistivity – Depending on soil type ranges from 1 – 50 ohms-meter

Calculated Data

- Resistance, Reactance, and Charging at 50o C and various lengths

- Sequence Series Impedance at 50o C and various lengths

- Shunt Admittance at 50o C and various lengths

# Mutual Impedance at 50o C and various lengths

# American Electric Power Service Corporation  Facility Ratings Calculations

In determining the thermal facility ratings of 69 kV and above, AEPSC incorporates Good Utility Practice with actual field data to ensure that the transmission system is in compliance with the ERCOT Reliability Criteria, AEPSC Transmission Planning Reliability Criteria, and North American Reliability Council (NERC). For additional information concerning the AEPSC transmission reliability criteria please download AEPSC Transmission Planning Standards Reliability Criteria located on the ERCOT ESPTO  web site at:

ftp://ftp.ercot-iso .com/transtud/Transtud.html

- Transmission Lines

- Existing transmission lines were designed to meet operating standards that were in effect at the time the line was built. The National Electric Safety Code (NESC) specified the maximum conductor temperature which maintained acceptable ground clearance while allowing for acceptable loss of conductor tensile strength. AEPSC Transmission Planning will use thermal ratings established by AEPSC Transmission Design that are consistent with the NESC design being practiced at the time the line was built.

- The thermal capabilities are generally assigned as shown in table “Existing Conductors Installed On System” for existing or future transmission lines. Lines with design constraints, existing or future, will be rated at actual design limits.

- The circuit thermal capabilities should be reduced to the ratings of the “Most Limiting Series Element” (MLSE) as described in the NERC Planning Standards IIC.S1/M1 and IIC.S1/M2. This includes but is not limited to substation terminal equipment; disconnect switches, wave traps, current transformers, and circuit breakers.

- The emergency ratings for transmission lines are for eight (8) hours.

- Disconnect Switches

Normal and emergency rating shall be 100% of nameplate rating.

- Wave Traps

Emergency rating shall be 110% of nameplate rating.

- Current Transformers

Normal and emergency rating shall be 100% of nameplate rating.

- Circuit Breakers

Normal and emergency rating shall be 100% of nameplate rating.

- Auto-transformers

- The normal rating for auto-transformers shall be its top nameplate rating, including the effects of forced cooling equipment if it is available.

- The emergency rating for auto-transformers shall be 110% of its top nameplate rating for the first four hours of emergency and 100% thereafter.

Input Data / Assumptions:

- Transmission Conductors

- Summer

- Wind Speed of 2 fps

- Ambient 40o C

- Normal Rating 85 o C

- Emergency Rating 100 o C

- Winter

- Wind Speed of 2 fps

- Ambient 20 o C

- Normal Rating 85 o C

- Emergency Rating 100 o C

- Auto-transformers

- Transformer ratings are calculated from manufacturer’s test data for continuos operation and are dependent upon the individual transformer

- Typically the ratings or calculated under these two standards:

- 55o C rise

- 65 o C rise

AEPSC uses the above describe assumptions, standards, and good utility practice in determining and applying the facility ratings described in section 1.5.1.4.1 Ratings Definitions for modeling criteria.

Appendix D

### Appendix E

| Original Request Number & Subtask Numbers | Data Sharing Requirements |
| --- | --- |
|  | Description of Request & Description of Sub-Task |
| 1 | Publish a listing of single element contingencies by SSWG bus numbers, that power-flow programs perform that are historically known to be invalid (or phantom) contingencies from a physical perspective due to modeling limitations. |
| 1.1 | TDSPs will provide in house exception files to ERCOT for Data Set A and for the first two years of Data Set B. This means that exception files for three years will be provided. Only exceptions that are currently known by TDSPs will be provided. |
| 1.2 | ERCOT will combine and post the individual files. |
| 1.3 | The same legal disclaimer that is used by ERCOT will apply to these files. |
| 2 | Publish a listing of the normal and emergency voltage limits that ERCOT Operations personnel will utilize to make voltage related congestion decisions. |
| 2.1 | ERCOT will post voltage profiles and limits as they become available, by 7/1/01. |
| 2.2 | ERCOT is in the process of developing limits and guides. |
| 3 | Publish a listing of all Special Protection Schemes (SPSs) and Remedial Action Plans (RAPs) that are being used, or are planned to be used, in ERCOT and post it on the ERCOT web site. |
| 3.1 | ERCOT will post all special protection schemes (SPSs) and remedial action plans (RAPs). |
| 3.2 | TDSPs will provide ERCOT the SPSs and RAPs. |
| 3.3 | ERCOT will provide RAPs. |
| 3.4 | ERCOT will post only the remedial action plans (RAPs) that impact CSC or OC congestion. RAPs that are for load serving reliability purposes only (i.e. transfer a transformer from a primary feed to an alternate feed during an outage of the primary. |
| 3.5 | ATC exceptions are currently posted. Informational purposes only, no additional task needs to be accomplished. |
| 3.6 | Create one common link, in the base case area of the ERCOT planning page, for data that is to be created or posted from the data sharing task force. |
| 4 | Provide a listing of all double-circuit lines by SSWG bus numbers that are greater than 0.5 miles (as defined by the ERCOT Planning Criteria) that will be used during planning studies, as well as the official "good weather" and "bad weather" contingencies |
| 4.1 | ERCOT to post double circuit file from the regional planning groups. |
| 4.2 | To the extent that TDSPs already have double circuit files, they will be sent to ERCOT to be posted by ERCOT until this task is superseded by the regional case postings. |
| 4.3 | ERCOT to post ESCA contingency "dump" with planning bus numbers of contingencies used for daily operational studies. |
| 4.4 | ERCOT translation file is already posted under the Texas Choice web site. This item is for informational purposes only; it requires no additional action. |
| 5 | Provide a listing by SSWG bus number of all special contingencies that should be included in power flow contingency studies to reflect the actual response of relay protection and sectionalizing facilities in place that constitute a single element outage (i.e. an auto-transformer connected to the line side of a breaker). The intent of this request is not to capture all in-line substations that aren't breakered; instead the intent is to capture all currently known special contingencies, such as the example given above, that impact transmission congestion studies. |
| 5.1 | ERCOT Operations intends to utilize "special" outages in its operational model. To the extent that a single element outage takes out additional elements in the system, these will be modeled in the operational model. An example may be the action of a relay. |
| 5.2 | To the extent that these situations are currently known by the TDSPs, they will be reported to ERCOT. An exhaustive study is not envisioned to be performed to discover these situations; they will be reported as discovered. |
| 5.3 | ERCOT will post as described in 4.3 above. |
| 6 | Publish an annual transmission plan document that is posted on the ERCOT web site that graphically and verbally illustrates the electrical connectivity (i.e. one-line representation) and proposed in-service date of all projects. |
| 6.1 | ERCOT will work with the TDSPs to develop and post on its web site a transmission project report annually that coincides with the release of Data Sets A and B. The report will be released in two sections in order to coincide with the release of both Data Sets A and B. |
|  | The report should only describe transmission projects of a commercial nature that can impact either CSC or OC congestion. TDSPs shall individually determine which projects have significance; however, as a minimum, the following types of projects should be included |
|  | 1) Construction of new lines |
|  | 2) Reconductor of existing lines |
|  | 3) Additions of auto-transformers |
|  | 4) Installation of FACTS devices or other devices intended to control the flow on circuits, i.e. series capacitors that are switched during contingencies or shunt capacitors. |
|  | 5) Installation of shunt reactive compensation devices (shunt capacitors, static var compensators, synchronous condensors, etc.) |
|  | Projects that can be impacted by the generation dispatch of nearby units whose capacity is 100 MW or greater will be reported. The intent is to capture for reporting purposes all of the projects that can impact how generation units are dispatched. |
|  | The form of submittal to ERCOT shall be determined individually by each TDSP to permit use of documents already generated internally. The project descriptions as a minimum should describe electrically where planned projects are located (simple one-line diagrams) |
| 6.2 | ERCOT will post the annual reports and updates. |
| 7 | Provide a project status report that is updated periodically and documents timing and scope changes to the transmission plan document that is posted annually. |
| 7.1 | Updates will be provided on 3/1 and 10/1 for projects that are listed in request 6 above. The targeted accuracy for the updates is to be within two weeks, i.e. 1st -15th or 15th - 30th. |
| 7.2 | Updates will be posted by ERCOT. |