## 2002 Trans Losses
TRANSMISSION LOSS FACTORS for 2002 as of 2/21/02 -(Version 3)
Data from Seasonal SSWG Base Cases Updated with Latest Model
Transmission Loss is from 60 kV or higher reporting only
NOIE INTERNAL refers to generation, load and losses behind NOIE meters
|  | ERCOT TOTAL |  |  |  | AEN NOIE INTERNAL TOTAL |  |  |  |  | CPS NOIE INTERNAL TOTAL |  |  |  |  | COG NOIE INTERNAL TOTAL |  |  |  |  | GEUS NOIE INTERNAL TOTAL |  |  |  |  | COD NOIE INTERNAL TOTAL |  |  |  |  | PUB NOIE INTERNAL TOTAL |  |  |  |  | Rayburn NOIE INTERNAL TOTAL |  |  |  |  | TEXLA NOIE INTERNAL TOTAL |  |  |  |  | COCS NOIE INTERNAL TOTAL
Case Type | Base Case Name | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV | Total Base Case Loss MW | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen)
Spring On Peak | 02SPG1 | 46700.1 | 45818.9 | 804.96 | 881.01 | 1067.8 | 2022.1 | 26.38 | 28.93 | 983.23 | 2297 | 2920.1 | 20.03 | 23.94 | 647.04 | 175.1 | 381.1 | 3.19 | 3.22 | 209.22 | 32.5 | 77.1 | 0.36 | 0.36 | 44.96 | 155.6 | 252 | 1.12 | 1.12 | 97.52 | 32 | 204 | 0.78 | 0.78 | 172.78 | 76 | 279.9 | 0.49 | 0.49 | 204.39 | 0 | 56 | 0 | 0 | 56 | 0 | 101.9 | 0.1 | 0.1 | 102
Spring Off Peak | 02SPG2 | 29553.7 | 29040.9 | 471.44 | 512.82 | 137.8 | 1103.8 | 16.55 | 16.65 | 982.65 | 1194 | 1621.7 | 4.45 | 6.5 | 434.2 | 38.5 | 127 | 0.8 | 0.8 | 89.3 | 12.3 | 31.9 | 0.06 | 0.06 | 19.66 | 82.5 | 123.5 | 0.32 | 0.32 | 41.32 | 0 | 115 | 0.33 | 0.33 | 115.33 | 76 | 196.2 | 0.23 | 0.23 | 120.43 | 0 | 39 | 0 | 0 | 39 | 0 | 86.5 | 0.08 | 0.08 | 86.58
Summer On Peak | 02SUM1 | 64410.9 | 63069.1 | 1223.72 | 1342.01 | 1405.1 | 2350.9 | 35.82 | 38.49 | 984.29 | 3438 | 4047.4 | 30.41 | 36.56 | 645.96 | 300.1 | 506.6 | 6.39 | 6.44 | 212.94 | 63.3 | 108 | 0.71 | 0.71 | 45.41 | 178 | 279 | 1.61 | 1.61 | 102.61 | 57 | 230 | 0.8 | 0.8 | 173.8 | 76 | 465.3 | 1.42 | 1.42 | 390.72 | 0 | 93 | 0.01 | 0.01 | 93.01 | 0 | 161.7 | 0.22 | 0.22 | 161.92
Summer Off Peak | 02SUM2 | 36920.1 | 36299.9 | 570.94 | 620.05 | 301.6 | 1269.4 | 16.38 | 16.87 | 984.67 | 1469 | 2150.9 | 7.99 | 10.14 | 692.04 | 81.5 | 169.9 | 1.59 | 1.6 | 90 | 13 | 32.6 | 0.06 | 0.06 | 19.66 | 101.9 | 142.8 | 0.5 | 0.5 | 41.4 | 0 | 126 | 0.4 | 0.4 | 126.4 | 76 | 247.1 | 0.37 | 0.37 | 171.47 | 0 | 49 | 0 | 0 | 49 | 0 | 128.8 | 0.13 | 0.13 | 128.93
Fall On Peak | 02FAL1 | 51951.8 | 50954 | 912.27 | 997.64 | 1092.8 | 2047 | 27.5 | 29.87 | 984.07 | 2707 | 3374.9 | 21.21 | 25.45 | 693.35 | 165.6 | 374.9 | 3.21 | 3.24 | 212.54 | 47.7 | 92.6 | 0.52 | 0.52 | 45.42 | 168.1 | 264.6 | 1.29 | 1.29 | 97.79 | 32 | 202 | 0.73 | 0.73 | 170.73 | 76 | 336.7 | 0.72 | 0.72 | 261.42 | 0 | 67 | 0.01 | 0.01 | 67.01 | 0 | 148.5 | 0.18 | 0.18 | 148.68
Fall Off Peak | 02FAL2 | 30819 | 30317.2 | 461.79 | 501.74 | 114.8 | 1081.7 | 14.96 | 15.03 | 981.93 | 1173 | 1851.7 | 5.55 | 7.45 | 686.15 | 39.5 | 128.1 | 0.85 | 0.85 | 89.45 | 12.3 | 31.9 | 0.06 | 0.06 | 19.66 | 93.9 | 134.9 | 0.37 | 0.37 | 41.37 | 0 | 125 | 0.41 | 0.41 | 125.41 | 76 | 199.2 | 0.23 | 0.23 | 123.43 | 0 | 40 | 0 | 0 | 40 | 0 | 116.3 | 0.11 | 0.11 | 116.41
Winter On Peak | 03WIN1 | 49215.4 | 48050 | 1085.58 | 1165.35 | 1030.8 | 1976.8 | 33.22 | 35.54 | 981.54 | 1960 | 2569.9 | 19.15 | 22.33 | 632.23 | 175.6 | 384.8 | 3.92 | 3.95 | 213.15 | 24.9 | 70 | 0.29 | 0.29 | 45.39 | 99 | 195.4 | 0.85 | 0.85 | 97.25 | 0 | 175 | 0.75 | 0.75 | 175.75 | 76 | 397.5 | 1.03 | 1.03 | 322.53 | 0 | 108 | 0.02 | 0.02 | 108.02 | 0 | 77.5 | 0.09 | 0.09 | 77.59
Winter Off Peak | 03WIN2 | 34546.2 | 33856.7 | 639.17 | 689.5 | 505.8 | 1457.5 | 27.55 | 28.35 | 980.05 | 1030 | 1692.1 | 5.84 | 7.37 | 669.47 | 47.9 | 136.5 | 1.32 | 1.33 | 89.93 | 18.3 | 37.9 | 0.09 | 0.09 | 19.69 | 28.8 | 69.8 | 0.22 | 0.22 | 41.22 | 0 | 97 | 0.24 | 0.24 | 97.24 | 76 | 275 | 0.47 | 0.47 | 199.47 | 0 | 75 | 0.01 | 0.01 | 75.01 | 0 | 66.9 | 0.06 | 0.06 | 66.96
Self Serve Load Modeled in Base Cases that does not contribute to transmission losses. | [8 empty] | NOIE TOTALS
Case Type | Base Case Name | RE HLP Self Serve MW | AEP Self Serve MW | TNMP Self Serve MW | BEC Self Serve MW | TXU Self Serve MW | CSWS DC Tie Model MW | TOTAL |  | NOIE LOAD MW | NOIE External Resources MW | NOIE Load Served from Internal Resources MW | NOIE TOTAL Loss Above 60 kV | Base Case Name
Spring On Peak | 02SPG1 | 2673.2 | 240.6 | 440 | 28 | 563.8 | 198.6 | 4144.2 |  | 6294.2 | 2517.14 | 3777.06 | 52.45 | 02SPG1
Spring Off Peak | 02SPG2 | 2673.2 | 240.6 | 440 | 28 | 563.8 | 198.6 | 4144.2 |  | 3444.6 | 1928.47 | 1516.13 | 22.82 | 02SPG2
Summer On Peak | 02SUM1 | 2673.2 | 235.1 | 440 | 28 | 563.8 | 198.6 | 4138.7 |  | 8241.9 | 2810.66 | 5431.24 | 77.39 | 02SUM1
Summer Off Peak | 02SUM2 | 2673.2 | 235.1 | 440 | 26.8 | 563.8 | 198.6 | 4137.5 |  | 4316.5 | 2303.57 | 2012.93 | 27.42 | 02SUM2
Fall On Peak | 02FAL1 | 2673.2 | 240.6 | 440 | 28 | 563.8 | 198.6 | 4144.2 |  | 6908.2 | 2681.01 | 4227.19 | 55.37 | 02FAL1
Fall Off Peak | 02FAL2 | 2673.2 | 240.6 | 440 | 28 | 563.8 | 198.6 | 4144.2 |  | 3708.8 | 2223.81 | 1484.99 | 22.54 | 02FAL2
Winter On Peak | 03WIN1 | 2673.2 | 176.4 | 440 | 28 | 563.8 | 198.6 | 4080 |  | 5954.9 | 2653.45 | 3301.45 | 59.32 | 03WIN1
Winter Off Peak | 03WIN2 | 2673.2 | 176.4 | 440 | 28 | 563.8 | 198.6 | 4080 |  | 3907.7 | 2239.04 | 1668.66 | 35.8 | 03WIN2
SEASON | ERCOT WITH SELF SERVE, MODEL & NOIE INTERNAL LOAD CORRECTIONS |  |  |  |  | AEN NOIE INTERNAL |  |  |  |  | CPS NOIE INTERNAL |  |  |  |  | COG NOIE INTERNAL |  |  |  |  | GEUS NOIE INTERNAL |  |  |  |  | COD NOIE INTERNAL |  |  |  |  | PUB NOIE INTERNAL |  |  |  |  | Rayburn NOIE INTERNAL |  |  |  |  | TEXLA NOIE INTERNAL |  |  |  |  | COCS NOIE INTERNAL
| SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF
SPRING | 42555.9 | 25409.5 | 1.892% | 1.855% |  | 2022.1 | 1103.8 | 1.288% | 1.477% |  | 2920.1 | 1621.7 | 0.6813% | 0.2737% |  | 381.1 | 127 | 0.8301% | 0.626% |  | 77.1 | 31.9 | 0.4648% | 0.1877% |  | 252 | 123.5 | 0.4425% | 0.2584% |  | 204 | 115 | 0.3809% | 0.2861% |  | 279.9 | 196.2 | 0.1748% | 0.1171% |  | 56 | 39 | 0% | 0% |  | 101.9 | 86.5 | 0.09804% | 0.0924%
SUMMER | 60272.2 | 32782.6 | 2.03% | 1.742% |  | 2350.9 | 1269.4 | 1.501% | 1.274% |  | 4047.4 | 2150.9 | 0.7457% | 0.3701% |  | 506.6 | 169.9 | 1.246% | 0.9272% |  | 108 | 32.6 | 0.6531% | 0.1837% |  | 279 | 142.8 | 0.5738% | 0.3489% |  | 230 | 126 | 0.3466% | 0.3165% |  | 465.3 | 247.1 | 0.3043% | 0.1495% |  | 93 | 49 | 0.01075% | 0% |  | 161.7 | 128.8 | 0.1359% | 0.1008%
FALL | 47807.6 | 26674.8 | 1.908% | 1.731% |  | 2047 | 1081.7 | 1.326% | 1.364% |  | 3374.9 | 1851.7 | 0.6245% | 0.2988% |  | 374.9 | 128.1 | 0.849% | 0.6592% |  | 92.6 | 31.9 | 0.5584% | 0.1877% |  | 264.6 | 134.9 | 0.4852% | 0.2735% |  | 202 | 125 | 0.3601% | 0.3269% |  | 336.7 | 199.2 | 0.2134% | 0.1153% |  | 67 | 40 | 0.01492% | 0% |  | 148.5 | 116.3 | 0.1211% | 0.09449%
WINTER | 45135.4 | 30466.2 | 2.405% | 2.098% |  | 1976.8 | 1457.5 | 1.653% | 1.855% |  | 2569.9 | 1692.1 | 0.7397% | 0.3439% |  | 384.8 | 136.5 | 1.008% | 0.9578% |  | 70 | 37.9 | 0.4126% | 0.2369% |  | 195.4 | 69.8 | 0.4331% | 0.3142% |  | 175 | 97 | 0.4267% | 0.2468% |  | 397.5 | 275 | 0.2584% | 0.1706% |  | 108 | 75 | 0.01852% | 0.01333% |  | 77.5 | 66.9 | 0.116% | 0.08961%
TRANSMISSION LOSS FACTORS FOR INSTALLATION IN ERCOT SYSTEMS IN RED BOXES
SEASON | ERCOT WITH SELF SERVE, MODEL & NOIE INTERNAL LOAD CORRECTIONS |  | For Testing Only |  |  | AEN NOIE INTERNAL |  | For Testing Only |  |  | CPS NOIE INTERNAL |  | For Testing Only |  |  | COG NOIE INTERNAL |  | For Testing Only |  |  | GEUS NOIE INTERNAL |  | For Testing Only |  |  | COD NOIE INTERNAL |  | For Testing Only |  |  | PUB NOIE INTERNAL |  | For Testing Only |  |  | Rayburn NOIE INTERNAL |  | For Testing Only |  |  | TEXLA NOIE INTERNAL |  | For Testing Only |  |  |  | COCS NOIE INTERNAL |  | For Testing Only
| SSC | SIC | 42555.9 |  |  | SSC | SIC | 2022.1 |  |  | SSC | SIC | 2920.1 |  |  | SSC | SIC | 381.1 |  |  | SSC | SIC | 77.1 |  |  | SSC | SIC | 252 |  |  | SSC | SIC | 204 |  |  | SSC | SIC | 279 |  |  | SSC | SIC | 108 |  |  |  | SSC | SIC | 100
SPRING | 2.1093e-06 | 1.8018 | 1.8915 |  |  | -0.00020629 | 1.7049 | 1.2878 |  |  | 0.00031393 | -0.23545 | 0.68126 |  |  | 0.00080332 | 0.52396 | 0.8301 |  |  | 0.0061288 | -0.0077738 | 0.46476 |  |  | 0.0014322 | 0.081562 | 0.44248 |  |  | 0.0010647 | 0.16369 | 0.3809 |  |  | 0.00068897 | -0.018085 | 0.17414 |  |  | 0 | 0 | 0 |  |  |  | 0.00036618 | 0.060726 | 0.097343
SUMMER | 1.0503e-05 | 1.3973 | 1.8442 |  |  | 0.00020977 | 1.0076 | 1.4318 |  |  | 0.00019807 | -0.055938 | 0.52246 |  |  | 0.00094586 | 0.76647 | 1.1269 |  |  | 0.0062255 | -0.01924 | 0.46075 |  |  | 0.0016507 | 0.11319 | 0.52918 |  |  | 0.00029005 | 0.27991 | 0.33908 |  |  | 0.00070916 | -0.025719 | 0.17214 |  |  | 0.00024435 | -0.011973 | 0.014417 |  |  |  | 0.001065 | -0.036347 | 0.070157
FALL | 8.3769e-06 | 1.5077 | 1.8642 |  |  | -3.9906e-05 | 1.4073 | 1.3266 |  |  | 0.00021383 | -0.097124 | 0.52729 |  |  | 0.000769 | 0.56066 | 0.85373 |  |  | 0.0061068 | -0.0070732 | 0.46376 |  |  | 0.0016317 | 0.053406 | 0.4646 |  |  | 0.00043061 | 0.2731 | 0.36095 |  |  | 0.00071313 | -0.026727 | 0.17224 |  |  | 0.00055271 | -0.022108 | 0.037584 |  |  |  | 0.00082521 | -0.0014784 | 0.081043
WINTER | 2.0942e-05 | 1.4599 | 2.3511 |  |  | -0.00038983 | 2.4233 | 1.6351 |  |  | 0.00045079 | -0.41884 | 0.89752 |  |  | 0.00020406 | 0.92992 | 1.0077 |  |  | 0.0054726 | 0.029491 | 0.45143 |  |  | 0.00094686 | 0.24811 | 0.48671 |  |  | 0.0023068 | 0.023052 | 0.49364 |  |  | 0.000717 | -0.026557 | 0.17349 |  |  | 0.00015708 | 0.0015508 | 0.018515 |  |  |  | 0.0024895 | -0.076941 | 0.17201