PDCWG Report

May 09, 2002

The PDCWG conducted a conference call on May 9th to finalize their comments on The NERC Policy 1 Frequency Standard.  The PDCWG is recommending a 400 MW/.1 Hz for an ERCOT standard.  This recommendation is based on the data collected from past disturbances.  The top 29 average frequency excursions during the year 2000, was 569.2MW/.1Hz.  The PDCWG believes that the wording in the policy about when response to frequency excursions begins isn’t clearly stated.  This wording should clearly distinguish the time it takes to establish a Point C and a Point B.

The frequency control consultant reported on the status of the frequency control work.