PARWG REPORT

June 17, 2002

The PAR Working Group attended a joint meeting with a WMS Task Force on June 4, 2002.  The purpose of the meeting was to assist the WMS in its TAC-requested review of the ROS’ Generation Adequacy Study.  Dr. Eugene Preston also attended to explain how the study was performed and answer questions.

WMS members expressed concern with the fact that the study was run using a ten percent forced outage rate for new combined cycle units.  Many WMS members believe these new generators will operate much more reliably.

To gain a ‘feel’ for the effect the FOR parameter had in the study, Dr. Preston was asked to run a few more studies to determine how a one percent improvement in FOR would affect the reserve margin needed to achieve a one-day-in-ten-year LOLE level.

The results of Dr. Preston’s work are attached and indicate that the FOR improvement would decrease the required reserve margin by about 1.5 percent.