| OGRR Number | 107-OGRR | OGRR Title | Recommended revisions resulting from the ERCOT SPWG review of the 1998 NERC DAWG Report |
| --- | --- | --- | --- |
| Date | June 21, 2002 |
| Submitter’s Information |
| Name | Rick Keetch |
| E-mail Address | rkeetch@reliant.com |
| Company | Reliant Energy |
| Company Address | P.O.Box 4567, Houston, TX, 77210 |
| Phone Number | 713-207-2526 |
| Fax Number | 713-207-0098 |

Instructions:

Comments are to be submitted electronically and are due by close of business of the comment due date.  Please follow this file naming convention:

###OGRR <Company Name> Comments<date>.doc.

Comments

[See below for language clarification, not meant to change the original intent.]

for faults beyond the zone it is designed to protect, shall be selective in time with other PRS, including breaker failure.

- Transmission line protection should consist of:

Primary phase and ground protection over a communications channel

Backup relaying with at least two zones of phase protection

Backup relaying with at least two zones of ground protection, or backup relaying with ground directional over current relaying (time delay and instantaneous)

"Ground chain protection" to recognize and trip for a three-phase fault right at the terminals, in service for a short period of time just as the line is energized, for lines with line side VTs

Recognition and trip for open conductor is desirable but not required

Overload protection is provided by SCADA analog alarms and dispatcher discretion

Fault detector relays to supervise phase distance relaying to prevent inadvertent trip due to VT failure

Short lines may require special attention, such as dual primary schemes, etc.

Fuses shall not be used in the 3Vo polarizing supply for ground relays

The setting for synchronization check relays should be based on system studies that identify the voltage angles necessary for a successful re-close.