| OGRR Number | 107-OGRR | OGRR Title | Recommended revisions resulting from the ERCOT SPWG review of the 1998 NERC DAWG Report |
| --- | --- | --- | --- |
| ###### Date |  | June 21, 2002 |  |
| ## Submitter’s Information |  |  |  |
| Name |  | Rick Keetch |  |
| E-mail Address |  | rkeetch@reliant.com |  |
| Company |  | Reliant Energy |  |
| Company Address |  | P.O.Box 4567, Houston, TX, 77210 |  |
| Phone Number |  | 713-207-2526 |  |
| Fax Number |  | 713-207-0098 |  |

Instructions:

Comments are to be submitted electronically and are due by close of business of the comment due date.  Please follow this file naming convention:

###OGRR <Company Name> Comments<date>.doc.

Comments

[See below for language clarification, not meant to change the original intent.]

- for faults beyond the zone it is designed to protect, shall be selective in time with other PRS, including breaker failure.

- Transmission line protection should consist of:

- Primary phase and ground protection over a communications channel

- Backup relaying with at least two zones of phase protection

- Backup relaying with at least two zones of ground protection, or backup relaying with ground directional over current relaying (time delay and instantaneous)

- "Ground chain protection" to recognize and trip for a three-phase fault right at the terminals, in service for a short period of time just as the line is energized, for lines with line side VTs

- Recognition and trip for open conductor is desirable but not required

- Overload protection is provided by SCADA analog alarms and dispatcher discretion

- Fault detector relays to supervise phase distance relaying to prevent inadvertent trip due to VT failure

- Short lines may require special attention, such as dual primary schemes, etc.

- Fuses shall not be used in the 3Vo polarizing supply for ground relays

- The setting for synchronization check relays should be based on system studies that identify the voltage angles necessary for a successful re-close.