| OGRR Number | 115-OGRR | OGRR Title | Change due to PRR219 Frequency Level Deviation |
| --- | --- | --- | --- |
| ###### Status |  | posted |  |
| Operating Guide Section Requiring Revision |  | 1.6 |  |
| Protocol Section Requiring Revision, if any. |  | ## None |  |
| Requested Resolution |  | ## Normal |  |
| Revision Description |  | Revise Operating Guides sections 1.6 to reflect that the correct frequency deviation contained in the Referenced Protocol 6.10.5.4. The frequency deviation in the referenced Protocol 6.10.5.4 is 0.375 Hz and should be 0.175 Hz. PRR 219, approved by the Board on 6-19-2001 and effective 7-01-2001, made these changes. Protocol references found in this section is also revised to reference the latest posted Protocols. |  |
| ###### Reason for Revision |  | - Current practice is to collect data from the existing Control Areas for deviations of 0.175Hz. There is no reason to change that practice under single control area operation. - Protocol references need to refer to the latest posted Protocols. |  |
| ## Sponsor |  |  |  |
| Name |  | Jack Thormahlen |  |
| E-mail Address |  | jack.thormahlen@lcra.org |  |
| Company |  | Lower Colorado River Authority |  |
| Company Address |  | P.O. Box 220, Austin, Texas 78767-0220 |  |
| Phone Number |  | 512-473-3200 ext. 2635 |  |
| Fax Number |  | 512-469-6856 |  |
| ## Timeline |  |  |  |
| Date Received |  | 06/26/2002 |  |
| Date Posted |  | 06/26/2002 |  |
| ROS Review Date |  |  |  |
| ROS Recommendation |  |  |  |
| Other Subcommittee Consideration |  |  |  |
| TAC Consideration |  |  |  |

Proposed Operating Guide Language Revision

Reference: Protocol 6.10.5.4.

For all frequency deviations exceeding  0.175 Hz, ERCOT shall measure and record each two (2) second scan rate values of real power output for each QSE Resource providing Responsive Reserve. ERCOT shall measure and record the MW data beginning one (1) minute prior to the start of the frequency excursion event until ten (10) minutes after the start of the frequency excursion event.

| ## Other TAC Subcommittee Review |  |
| --- | --- |
| PRS Review Date |  |
| PRS Protocols Impact Decision |  |
| WMS Review Date |  |
| RMS Review Date |  |
| ## TAC Action |  |
| TAC Vote Date |  |
| TAC Proposed Implementation Date |  |
| TAC Vote Results |  |