| OGRR Number | 107OGRR | OGRR Title | Recommended revisions resulting from the ERCOT SPWG review of the 1998 NERC DAWG Report |
| --- | --- | --- | --- |
| ###### Status |  | Posted |  |
| Operating Guide Section Requiring Revision |  | Appendix B Section B.4.5.2 subsection “Environment” Appendix B Section B.4.5.3 subsection “Transmission Line Protection” |  |
| Protocol Section Requiring Revision, if any. |  | ## None |  |
| Requested Resolution |  | ## Normal |  |
| Revision Description |  | To address the potential for ice-related attenuation of power line carrier blocking signals (B.4.5.2) and the potential for a catastrophic failure during a synchronous check relay assisted reclosing attempt (B.4.5.3). |  |
| ###### Reason for Revision |  | Provide guide for consideration in setting of protective relay systems. This resulted from the SPWG annual review of the NERC Disturbance Analysis Working Group. This recommendation was presented by the SPWG at the 12/10/2001 ROS meeting. ROS asked SPWG to file an OGRR. |  |
| ## Sponsor |  |  |  |
| Name |  | Sergio Garza, Chair ERCOT System Protection Working Group |  |
| E-mail Address |  | Sgarza@lcra.org |  |
| Company |  | Lower Colorado River Authority |  |
| Company Address |  | P.O. Box 220 Austin, Texas 78767-0220 |  |
| Phone Number |  | (512) 369-7249 |  |
| Fax Number |  | (512) 369-7289 |  |
| ## Timeline |  |  |  |
| Date Received |  | 02/08/2002 |  |
| Date Posted |  | 02/08/2002 |  |
| ROS Review Date |  | 07/11/2002 |  |
| ROS Recommendation |  | 07/12/2002 |  |
| Other Subcommittee Consideration |  | 07/22/2002 [PRS] |  |
| TAC Consideration |  |  |  |

Proposed Operating Guide Language Revision

#### B.4.5.2	Equipment and Design Considerations

Environment

- Means shall be employed to maintain environmental conditions that are favorable to the correct performance of PRS.  Particular attention should be given to solid-state equipment installations.

- Other environmental hazards to look out for:

| - Fire ants | - Rats |
| --- | --- |
| - Snakes | - Dust, dirt, grime |
| - Trash and leftover hardware | - Water |
| - Gunfire | - Theft of substation and transmission grounds |
| - Hand-held radio keyed near solid-state relays | - Batteries located in same room as relays (battery fires) |
| - Severe cold weather conditions can impact operation of circuit breakers, DC battery, and carrier signals. |  |

#### B4.5.3	Specific Application Considerations

Transmission Line Protection

- Each of the two independent PRS shall detect and initiate action to clear any line fault without undue system disturbance.  The PRS shall operate for line faults so that, if ultimate clearing should be accomplished by a breaker failure scheme, a widespread disturbance will not result.  A PRS, which can operate for faults beyond the zone it is designed to protect, shall be selective in time with other PRS, including breaker failure.

- Transmission line protection should consist of:

- Primary phase and ground protection over a communications channel

- Backup relaying with at least two zones of phase protection

- Backup relaying with at least two zones of ground protection, or backup relaying with ground directional overcurrent relaying (time delay and instantaneous)

- "Ground chain protection" to recognize and trip for a three-phase fault right at the terminals, in service for a short period of time just as the line is energized, for lines with line side VTs

- Recognition and trip for open conductor is desirable but not required

- Overload protection is provided by SCADA analog alarms and dispatcher discretion

- Fault detector relays to supervise phase distance relaying to prevent inadvertent trip due to VT failure

- Short lines may require special attention, such as dual primary schemes, etc.

- Fuses shall not be used in the 3Vo polarizing supply for ground relays

- Where used, settings for sync check relays should be based upon appropriate system studies where the acceptable voltage angles are identified for a successful re-close.

| ## Other TAC Subcommittee Review |  |
| --- | --- |
| PRS Review Date | 7/22/2002 |
| PRS Protocols Impact Decision | None. |
| WMS Review Date |  |
| RMS Review Date |  |
| ## TAC Action |  |
| TAC Vote Date |  |
| TAC Proposed Implementation Date |  |
| TAC Vote Results |  |