| OGRR Number | 117OGRR | OGRR Title | Communicating with ERCOT |
| --- | --- | --- | --- |
| Operating Guide Section Requiring Revision |  | Appendix C |  |
| Protocol Section Requiring Revision, if any. |  |  |  |
| Revision Description |  | Revise Appendix C to include protocol references with language from the Protocols, replace references to “Communicating with ERCOT” with language from the document, and include the requirement for a backup source for Weather Zone tie-line data. Various language changes are proposed throughout the document in an attempt to clarify the ERCOT real-time data requirements for TDSPs and QSEs. |  |
| ###### Reason for Revision |  | The proposed revision of Appendix C will reduce the dependency of the Operating Guides to a document (“Communicating with ERCOT” ) written by the ERCOT staff. The revision will serve to clarify ERCOT real-time data requirements from the TDSPs and QSEs to ERCOT. |  |
| ## Sponsor |  |  |  |
| Name |  | Eddie Clark, ERCOT Network Data Support Working Group Chair |  |
| E-mail Address |  | eclark@oncorgroup.com |  |
| Company |  | Oncor |  |
| Company Address |  | 2233-C Mountain Creek Pkwy, Dallas, TX. 75211-6716 |  |
| Phone Number |  | 214-743-6841 |  |
| Fax Number |  | 214-743-6704 |  |

These comments are the combined effort of the Network Data Support Working Group (NDSWG), ERCOT and the Operating Guides Revision Task Force (OGRTF).

Proposed Operating Guide Language Revision

## Operational Metering

QSE control centers supply operational metering data to ERCOT and receive signals from ERCOT to implement frequency control.  The QSE’s interface to ERCOT for this purpose is implemented through a QSE-supplied RTU or other device using DNP 3.0 protocol at the QSE control center.

TDSPs supplying operational metering to ERCOT shall use an ICCP interface through the ERCOT WAN  TDSPs may use an RTU interface similar to QSE’s only with approval from ERCOT.

Each QSE or TDSP shall continuously provide the data quantities that they are responsible for providing to ERCOT.  The frequency of update, means of communication to ERCOT, and format for each point shall also be as specified in Attachment A for that entity, unless approved by ERCOT.  At the frequency specified in the Tables, each update cycle shall provide new readings of all data points being monitored, not averages linked to prior cycle readings or repetition of readings from a previous cycle.  Inaccuracy for data points as delivered to ERCOT, when compared with actual quantity measured at the source, shall be no greater than 4%.

Reference Protocols, Section 12.4.4.1.1

QSEs, Resources and TDSPs are required to provide power operation data to ERCOT including, but not limited to:

            - Real time generation data from QSEs;

            - Planned Outage information from Resources;

            - Network data used by any TDSP’s control center, including:

              - Breaker and line switch status of all ERCOT Transmission Grid devices;

              - Line flow MW and MVAR;

              - Breaker, switches connected to all Resources;

              - Transmission Facility Voltages; and

              - Transformer MW,  MVAR, and TAP.

            - Real time generation and Load acting as a Resource meter data from QSEs;

            - Real time Generation meter splitting signal from QSEs;

            - Planned Transmission Outage information from TDSP;

            - Network transmission data (model and constraints) from TDSP;

            - Resource Plans from QSE; and

            - Dynamic Schedules from QSEs;

Real Time data will be provided to ERCOT at the same scan rate as the TDSP or QSE obtains the data from telemetry.

### ERCOT Interface RTUs

ERCOT interface RTUs pass communications between the Market Participant  responsible for supplying Operational Metering data and ERCOT.   Suppliers of data must install and configure these RTUs according to ERCOT procedures. The RTU or other device shall reflect the data quality codes (ie. suspect, failed, manual, etc) of the individual data points found in the Market Participant’s  control computers and data collection systems.

#### C.2.1.1

In order to ensure that real-time data can be exchanged in a timely manner, the connection concept has been extended to support the use of specified communications protocols. Specifically, the 2-second data sent to ERCOT, and the 4-second data received from ERCOT required for frequency control will be exchanged via DNP 3.0 communications protocol. The connection is designed around the following requirements:

The connection paths begin with the Market Participant’s RTU or SCADA system.  Three serial ports provide for the redundant paths,  two to the Point-to-Point network and one to the Frame Relay network. The path to the Point-to-Point network is passed through a modem, and the modulated signal connects to the Market Participant’s Channel Bank. Voice circuits to be placed on the Point-to-Point network are combined with the data circuit on a Fractional T1 connected between the Channel Bank and the Point-to-Point network CSU/DSU. RTU data sent over the Point-to-Point network will employ DNP 3.0.

The path to the Frame Relay network is accomplished by connecting the RTU/SCADA to a data Gateway via a serial interface. The Gateway communicates with the RTU/SCADA using DNP 3.0 only. The Gateway then exchanges the data with a compatible Data Server at ERCOT. The protocol used for this data exchange is TCP/IP.

This connection design supports redundancy for both data exchange and voice circuits between the Market Participant and ERCOT. Data exchange redundancy is provided as described here. The Public Switched Telephone Network (PSTN) provides backup for voice circuits.

### C.2.2  ERCOT ICCP Interface

Inter-Control Area Communications Protocol (ICCP) over Ethernet provides Operational Metering data from Market Participant computers, computer networks, or other devices to the ERCOT WAN.  Suppliers of data using an ICCP link must format their data and coordinate installation according to ERCOT procedures.  The data furnished by a Market Participant’s  ICCP link shall reflect the data quality codes (ie, suspect, failed, manual, etc) of the individual data points found in the Market Participant’s control computers and data collection system.

### C.2.3  Validation of Real Time Signals with Settlement Metering for Resources

The integrated real time MW signal obtained from a resource shall be validated .

Signals from resources used to supply power or ancillary services shall be integrated by ERCOT and checked against settlement meter values on a monthly basis.

Where multiple generators share a single net settlement meter, the ratio of integrated real time signals from each generator shall be used to proportion the settlement total quantity.

- Data from ERCOT to QSE’s

ERCOT shall issue instructions and information to QSE’s in accordance with the Operating Guide and the Protocols.  Attachment A provides the instructional and informational data sets that ERCOT will send to the QSEs to satisfy the requirements in the Operating Guide and the Protocols.

### C.2.5  Data From ERCOT to TDSP

ERCOT will provide operational data and issue instructions to the TDSP in accordance with the Operating Guide and the Protocols.

Reference Protocols, Section 12.4.4.1.2,

ERCOT is required to provide the following power operation data to TDSPs, in accordance with confidentiality as defined in Section 1.3, Confidentiality of these Protocols:

            - Relevant information for the purpose of providing reliability as determined by ERCOT, including but not limited to:

              - Status of any breakers and switches in ERCOT's Real Time data base;

              - State estimator solutions;

              - Transmission line flows and voltages;

              - Transformer information;

              - QSE Resource data;

              - Voltage schedules at major transmission busses;

ERCOT will give notice to the Entities supplying the above list of data to ERCOT upon the initial provision of such data to the TDSP.

### C.2.6  Data from QSE/TDSP to ERCOT

QSEs and TDSPs shall provide Real Time Monitoring of power system quantities to ERCOT as defined in the  Operating Guide and the Protocols. Attachment A gives the format and parameters for the content of each type of data point that ERCOT may request from TDSPs and QSEs to satisfy the requirements in the Operating Guide and the Protocols. Not all points in Attachment A are necessarily required from each entity.  ERCOT will inform TDSPs and QSEs if additions to presently furnished data are required.  Both parties will seek to jointly resolve a means and schedule for providing data to ERCOT, including changes to existing data.  ERCOT will consider alternatives and exceptions, on a case-by-case basis, to the extent that ERCOT does not believe its operational needs are compromised.   Ultimately, it is the responsibility of the TDSP or QSE to provide all data requested by ERCOT that is set forth in the ERCOT Protocols and Operating Guide.  Additional points and amendments shall be based on ERCOT operational needs and will be presented to the appropriate ERCOT TAC Subcommittees for approval for changes to the Protocols or the Operating Guide.

All real time monitoring data for a TDSP will be provided to ERCOT through a primary ICCP association.  If the TDSP is responsible for providing Weather Zone data, they are required to establish a backup to the primary source using one of the options below:

1.	TDSPs having an EMS with a native ICCP application capable of 4 second periodic data set transfers with minimum 300 points per data set, and hot standby backup ICCP servers with automatic failover capability, shall provide an additional ICCP association across the ERCOT WAN for the transfer of Weather Zone tie line measurements.  ICCP nodes should exist at primary and backup facilities.

2.	TDSPs not having an EMS with a native ICCP application shall install a RTU with three DNP 3.0 ports for ERCOT's use to provide Weather Zone tie measurements.  The data that ERCOT receives from the RTU shall reflect the EMS data quality codes.  RTUs should exist at primary and backup facilities.

### C.2.7  TDSP/QSE Metering Restoration

Operational Meter data shall be provided continuously.  Lost data or signals, whether failed or in error, must be restored promptly by the provider of Operational Metering data.  It is recognized that some data may be more critical that other data.  ERCOT will inform the TDSP or QSE if a data item is critical and needs to be repaired as quickly as possible.  QSE and TDSP repair procedures and records shall be made available to ERCOT upon request.

### C.2.8  QSE and TDSP Data Acquisition

Suppliers of Operational Metering must collect and process field data at their control centers before passing to the ERCOT interface.  The equipment and processes are owned and operated entirely by the supplier.  Traditionally, utilities have used both analog and digital methods of transmission at existing facilities.  It is the responsibility of the QSEs and TDSPs who supply other entities’ data to ERCOT to also arrange for reliable delivery of field data from the other entities in order to support the requirements in this Operating Guide.

### C.2.8

#### C.2.8.1

#### C.2.8.2

#### C.2.8.3

#### C.3  Calibration and Testing

#### C.3.1   Responsibility

It is the responsibility of the owner to insure that calibration, testing and other routine maintenance of equipment is done on a timely basis, and that accuracy meets or exceeds that which is specified in this Appendix, for both the overall system and for individual equipment where detailed herein.  Coordination of outages required for these activities with ERCOT is also the responsibility of the owner.

#### C.3.2  Notification

ERCOT and all affected parties shall be notified at least 72 hours in advance, or at a mutually acceptable advance notice, prior to any calibrations or planned maintenance. In emergency conditions, the owner of the operational metering and associated equipment may make necessary repairs with notification to affected parties within 24 hours.  ERCOT or other parties sharing data from the equipment may request copies of the repair and calibration records.

#### C.3.3  Test Equipment

Test equipment and test standards intended to be used for the calibration of operational metering and associated equipment shall be certified to values of accuracy and precision that are equal to or better than the accuracy of the equipment under test.

#### C.2.9.4

#### .

#### C.3.4  Disputes

Where a dispute over the accuracy or performance of any operational metering equipment exists, ERCOT may request a comparison of standards and/or a joint calibration of affected equipment.

#### C.3.5  Calibration Testing

All operational metering and associated equipment for analog data quantities (MW, MVAR, Volts, LTC tap positions, etc.) shall be tested as needed to ensure accuracy and performance. Entities providing Operational Metering data to ERCOT shall make their test records, procedures and maintenance criteria available to ERCOT upon request.

## C.4  Exchange of Information

Reference Protocols, Section 8.7.1

Prior to energizing and placing into service any new or relocated piece of equipment connected to the ERCOT Transmission Grid, TSPs shall coordinate with and receive approval from ERCOT.

#### C.4.1  Documentation

Reference Protocols, Section 8.7.2.1

The TSP shall notify ERCOT at least 30 days before starting to energize or place into service any new or relocated piece of equipment. The notice shall include:

(1)	TSP performing work;

(2)	Location Code if applicable;

(3)	Identification of existing Transmission Facilities involved and new Transmission Facilities (if any) being added or existing Transmission Facilities being permanently removed from service;

(4)	Outages required (clearly identify each Outage if multiple outages are required), including sequence of Outage and estimate of Outage duration;

(5)	General statement of work to be completed with intermediate progress dates and events identified;

(6)	Supervisory Control and Data Acquisition modification work;

(7)	Complete descriptions of any new data telemetry points or changes to existing telemetry;

(8)	Procedure for reporting work accomplished, including reporting to ERCOT, TSP and the QSE representing the Resources involved;

(9)	General description of the method to be used to energize and test new/rebuilt Transmission Facilities.

(10)	In service testing, including:

              - Procedure to be performed;

              - Notice of testing completion.

(11)	Statement of completion, including:

              - Statement to be made at the completion of each section of program;

              - Statement to be made at completion of total project.

(12)	Drawings to be attached, including:

              - Existing status;

              - For each intermediate stage;

              - Proposed completion of job.

The parties involved shall furnish pertinent information to ERCOT on request, including the following:

- Connection diagrams

- Metering one line diagram

- Substation one line diagram

- Panel schematics and one line diagrams

- Instrument transformer (CT and PT) data (ratios, test reports, nameplate)

- Transducer conversion constants

- Meter constants

- RTU and digital device configuration details

- Certified calibration test reports of any device used for operational metering

- Other data as may be requested

#### C.4.2  Operator One-line Displays

Operations staff at each entity providing Operational Metering data shall have one-line diagrams displayable on their Energy Management System or other computer systems.  Displays shall be provided for all substations or power plant switchyards that include data passed to the ERCOT interface.

#### C.4.3  Notification of Changes

Reference Protocols, Section 8.7.2.31

The TSP shall notify ERCOT and any other affected TSPs as soon as practicable of any requested changes to the work.  ERCOT shall review and approve or reject changes to the work in accordance with Section 8.7, Coordination for System Topology Modifications.

ERCOT and any other affected parties shall be informed of changes to operational metering and associated equipment 30 days prior to placing in service.  All parties must be notified so a mutually agreeable time can be set for the changes.  All parties involved must be satisfied prior to the making of any changes.

## C.5  Communications

There are two types of data communication that will be implemented in the ERCOT System:

  - Real-Time Communications (Operational), and

  - Commercial Market Communications (Settlement).

This Operating Guide defines the path standards for real-time data communications (Operational) and voice communications (Operational) that shall be used to exchange security and reliability information between:

  - ERCOT and a QSE, and

  - ERCOT and a TDSP.

As Operational signals may originate with or be destined for organizations connected to a QSE or TDSP, path standards are also defined for real-time data communications (Operational) and voice communications (Operational) required by QSEs and TDSPs that impact or contribute to security and reliability information required by ERCOT.

Commercial Market Communications (Settlement) are not defined in this Operating Guide, other than facilities needed to provide common communications.  Operational Communication requirements take precedence over Commercial Market Communication requirements.

### C.5.1  ERCOT WAN

In order to facilitate wholesale operations and frequency control as a single control area, ERCOT provides a wide area network (the ERCOT WAN).  This communications network uses redundant, digital communications between ERCOT control centers and one or more facilities at each QSE and TDSP.  The ERCOT WAN has sufficient bandwidth capacity and speed to enable:

  - Real time (operational metering) data exchange for frequency control and transmission security

  - Operational voice communications for both normal and emergency use.  The ERCOT WAN supports both off-premise exchanges (OPX) with ERCOT’s control facilities and the ERCOT hotlines.

  - Data exchange to support applications programming interface (API) routines.  These include power scheduling, operating plans, outage requests, dispatch instructions, posting of information and other applications.

### C.5.2  ERCOT Responsibilities

ERCOT supplies interface requirements, equipment, installation and 24-hour maintenance for the entire ERCOT WAN, including equipment at each QSE and TDSP control facility, as well as ERCOT’s control centersERCOT’s responsibilities include:

    - Supply and install fully configured and tested Customer Premises Equipment including routers, CSU/DSUs, LAN switch/hub and all support equipment for management purposes.

    - Order and provision of local loop, network access point and transport.

    - Design, configure, test, and install network monitoring and management service.

    - Provide 24-hour network monitoring and management.

    - Provide 24X7 maintenance, with 4-hour response, for all ERCOT equipment located at participant site.

    - ERCOT will be the single point of contact for all network issues.

### C.5.3  QSE and TDSP Responsibilities

TDSPs and QSEs whose facilities connect to the ERCOT WAN are required to sign an agreement with ERCOT governing installation, operation and maintenance.  Users of the ERCOT WAN shall provide signal connections, uninterruptible power, and physical space for ERCOT-supplied WAN interface equipment at their control centers, as well as 24-hour access for ERCOT installation and maintenance personnel.

At these facilities, computer and communications equipment connected to ERCOT WAN interfaces is the complete responsibility of the QSE or TDSP.   Facilities shall have uninterruptible power supplies (UPS) capable of independently supplying all equipment connected to the ERCOT WAN for at least 72 hours.

Any TDSP or QSE facility, whether primary or backup, involved in the transfer of the data sets identified in Attachment A, will be required to connect directly to the ERCOT WAN Frame Relay and Point-to-Point paths. If a TDSP and QSE utilize the same EMS and server network at one location and do not have an equipped backup center, ERCOT will only connect to this one location for the transfer of data.  If a TDSP and QSE share a centralized PBX, separate OPX circuits will be terminated for each participant.  The Hotline will not be allowed to connect through the PBX system and is required for each participant.

A QSE or TDSP involved in the transfer of the critical data identified in Attachment A, will be required to provide the following communication resources to support the connection to the ERCOT private network:

- Private Network

  - Provide an analog business phone line or PBX analog extension for trouble-shooting and maintenance of equipment.

  - Provide a height of 24” of rack space in a 19” wide rack.

  - Provide two separate UPS single-phase 115 VAC 20 amp circuits, each with 4 receptacles in the 19” rack listed above.

  - Provide building wiring from circuit termination to equipment rack.

  - Within 24-hours notice, provide ERCOT employees or contractors access to the communication facility.

  - Within 1-hour notice, provide emergency access to the facility to ERCOT employees or contractors.

  - Provide on site personnel to escort ERCOT employees or contractors.

  - Provide a Firewall or router, located at the Market Participant site, for the network address translation of internal Market Participant addresses to external addresses on the ERCOT LAN.

  - Market Participant will be required to sign a security connection agreement with ERCOT.

  - Provide connectivity from Market Participant Firewall or Router to ERCOT LAN located at Market Participant site. Market Participants are responsible for their own security through this connection.

  - Provide a channel bank with at least one T1 interface, 4 FXS and two 4 wire analog ports. Connect FXS (e.g. PBX, key system) and 4 wire ports to the appropriate equipment (e.g. RTU).  On the digital T1 stream, levels for voice are zero dpm for transmit and receive and levels for RTU are –13 dpm for transmit and receive.

  - Hotline must be a 500 set not attached to the Market Participant’s Phone System.

  - Dual cable entrances to Market Participant, connecting to different Telco Central Offices highly recommended.

  - Provide ERCOT with internal IP addressing scheme as needed for network design. This will be kept confidential.

- Internet (optional)

A QSE or TDSP NOT involved in the transfer of the data identified in Attachment A, is not required to, but, may request ERCOT to provide an optional connection to the ERCOT private network.  When such a request is met by ERCOT, the QSE or TDSP must then provide the above stated communications resources.

### C.5.4  TDSP and QSE Supplied Communications

Each TDSP and QSE must provide internal facilities and communications to collect and furnish data and voice signals to the ERCOT WAN.  For TDSPs these include, but may not be limited to, voice communications and SCADA for substations and other transmission facilities.  For QSEs, these include, but may not be limited to, voice and SCADA for generating plants and loads.

QSEs and TDSPs shall supply, implement and maintain all data and voice communication facilities required to fulfill the obligations set forth in the Operating Guide.

Proper performance, maintenance and testing of communication paths not directly connected to the ERCOT WAN shall be the responsibility of the TDSP or QSE providing the path.

QSEs communicating with connected resources and TDSPs communicating with substations are encouraged to use privately owned communication facilities.  Backup facilities utilizing common carriers, different privately owned facilities, or communications paths to a site are encouraged to provide increased reliability (i.e., separate paths to a site using different carrier, having multiple microwave paths leaving a site, etc.).

### C5.5  Maintenance and Restoration

It is the joint responsibility of ERCOT WAN-connected parties to coordinate maintenance and restoration activities so its reliability is not compromised.  Coordination and notification procedures defined by ERCOT are to be followed by all parties.

All circuits shall be tested annually or as otherwise requested by ERCOT for end-to-end performance.  Special attention shall be given to circuits not used for routine communications (including backup circuits).

The hotline and any backup (alternate path) voice circuits shall be used regularly to insure proper performance.  ERCOT will specify test procedures for hotline circuits.

Scheduled outages of communication circuits that could reduce the reliability of interconnected operations shall be coordinated between the affected companies and ERCOT.

In the event of wide spread communication failures, priority shall be given to restoring communication circuits between QSE Control Centers/TDSP Control Centers and ERCOT Control Area Authority first, and between QSEs and TDSPs second.

Test equipment and test standards intended to be used for the calibration or repair of communication equipment shall be certified to values of accuracy and precision which are equal to or better than the accuracy of the equipment under test.

- Attachment A:	 ERCOT Data Sets

For any required data, the following table describes how the data is to be provided to ERCOT.

| ACTION | DATA QUANTITY | PURPOSE | SUPPLIED BY | RECEIVED BY | FREQUENCY | MODE OF COMM. | FORMAT | PROTOCOLS REFERENCE / COMMENTS |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| DAY-AHEAD SCHEDULING PROCESS |  |  |  |  |  |  |  |  |
| Extend Day-Ahead Scheduling Process | Notification to extend Day-Ahead Scheduling Process to Two-Days-Ahead | Emergency Notification | ERCOT | QSE | Demand | API | XML | Protocols Section 4.4.19, Decision to Extend Day-Ahead Scheduling Process to Two-Day-Ahead Scheduling Process |
| Day Ahead Notification | Transmission Outages | Day-Ahead Planning | ERCOT | QSE | Daily before 0600 | API | XML | Protocols Section 4.4.2, Advance Publication of Forecasted System Conditions |
|  | Total Transmission Capacity | Day-Ahead Planning | ERCOT | QSE | Daily before 0600 | API | XML | Protocols Section 4.4.2, Advance Publication of Forecasted System Conditions |
|  | Weather assumptions used by ERCOT to forecast system conditions | Day-Ahead Planning | ERCOT | QSE | Daily before 0600 | API | XML | Protocols Section 4.4.2, Advance Publication of Forecasted System Conditions |
| Day-Ahead Notification | Ancillary Services (AS) Plan | Day-Ahead Planning | ERCOT | QSE | Daily before 0600 | API | XML | Protocols Section 4.4.3, Notification to the Market of ERCOT's Day-Ahead Ancillary Services Plan |
|  | Ancillary Service Obligations | Day-Ahead Planning | ERCOT | QSE | Daily by 0600 | API | XML | Protocols Section 4.4.4, Notification to QSEs of Ancillary Service Obligations |
|  | Mandatory Balancing Energy Service Down Bid Percentage requirements | Day-Ahead Planning | ERCOT | QSE | Daily by 0600 | API | XML | Protocols Section 4.4.5, Notification to QSEs of Mandatory Balancing Energy Service down Bid Percentage Requirements |
|  | Transmission and Distribution Loss Estimates | Day-Ahead Planning | ERCOT | QSE | Daily by 0600 | API | XML | Protocols Section 4.4.6, Notification to QSEs of Transmission Loss Estimates |
|  | Update of Forecasted System Conditions (total forecast system load and load forecasts in each congestion Zone) | Day-Ahead Planning | ERCOT | QSE | Daily @ 0600 | API | XML | Protocols Section 4.4.7, Update of Forecasted System |
| QSEs Submit Balanced Schedules of Obligations and Supply | Balanced Schedules | CSC Congestion and Capacity Insufficiency | QSE | ERCOT | Daily before 1100, @ 1300, then as needed | API | XML | Protocols Section 4.4.8 & 4.4.10, Submittal of Day-Ahead Schedules and Ancillary Services Schedules |
| Self-Arranged Ancillary Services | Self Provided Regulation Up | AS (Rolled up from REP to QSE) | QSE | ERCOT | Daily before 1100, @ 1300, then as needed | API | XML | Protocols Section 4.4.8 & 4.4.10, Submittal of Day-Ahead Schedules and Ancillary Services Schedules |
|  | Self Provided Regulation Down | AS (Rolled up from REP to QSE) | QSE | ERCOT | Daily before 1100, @ 1300, then as needed | API | XML | Protocols Section 4.4.8 & 4.4.10, Submittal of Day-Ahead Schedules and Ancillary Services Schedules |
|  | Self Provided Responsive Reserve | AS (By Portfolio) | QSE | ERCOT | Daily before 1100, @ 1300, then as needed | API | XML | Protocols Section 4.4.8 & 4.4.10, Submittal of Day-Ahead Schedules and Ancillary Services Schedules |
|  | Self Provided Non-Spinning Reserve | AS (By Portfolio, By Zone) | QSE | ERCOT | Daily before 1100, @ 1300, then as needed | API | XML | Protocols Section 4.4.8 & 4.4.10, Submittal of Day-Ahead Schedules and Ancillary Services Schedules |
| Validate Schedules and Bids | Notification of invalid or mismatched schedules | Validate Schedules | ERCOT | QSE | Daily @ 1100 & 1300 | API | XML | Protocols Section 4.4.12, ERCOT Validation of Qualified Scheduling Entity's Day-Ahead Schedules and Bids |
|  | Corrected Schedules | Submit corrected information | QSE | ERCOT | Daily @ 1115 & 1315 | API | XML | Protocols Section 4.4.12, ERCOT Validation of Qualified Scheduling Entity's Day-Ahead Schedules and Bids |
|  | Notification of CSC Congestion and/or Capacity Insufficiency | Update Schedules | ERCOT | QSE | Daily by 1115 | API | XML | Protocols Section 4.4.9, ERCOT Notification of CSC Congestion and/or Capacity Insufficiency based on 1100 |
| Procure Ancillary Services | AS Bids to ERCOT | Ancillary Services Market | QSE | ERCOT | Daily by 1300 | API | XML | Protocols Section 4.4.11, Ancillary Services Bid |
|  | Purchase Regulation Up | Complete Day-Ahead Ancillary Services Plan | ERCOT | QSE | Daily by 1330 | API | XML | Protocols Section 4.4.13, ERCOT Day-Ahead Ancillary Services Procurement Process |
|  | Purchase Regulation Down | Complete Day-Ahead Ancillary Services Plan | ERCOT | QSE | Daily by 1330 | API | XML | Protocols Section 4.4.13, ERCOT Day-Ahead Ancillary Services Procurement Process |
|  | Purchase Responsive Reserves | Complete Day-Ahead Ancillary Services Plan | ERCOT | QSE | Daily by 1330 | API | XML | Protocols Section 4.4.13, ERCOT Day-Ahead Ancillary Services Procurement Process |
|  | Purchase Non-Spinning Reserves | Complete Day-Ahead Ancillary Services Plan | ERCOT | QSE | Daily by 1330 | API | XML | Protocols Section 4.4.13, ERCOT Day-Ahead Ancillary Services Procurement Process |
|  | Ancillary Services Schedules | Notification of Selected Ancillary Services Bids | ERCOT | QSE | Daily by 1330 | API | XML | Protocols Section 4.4.14, ERCOT Day-Ahead Ancillary Services Procurement Process |
|  | Publish Day-Ahead MCPs for Capacity (MCPCs) for each Day-Ahead Ancillary Service | Complete ERCOT's Day-Ahead Ancillary Services Plan | ERCOT | QSE | Daily @ 1330 | API | XML | Protocols Section 4.4.13, ERCOT Day-Ahead Ancillary Services Procurement Process |
|  | Final Ancillary Services Schedules | Updated Day Ahead Ancillary Services Schedule | QSE | ERCOT | Daily @ 1500 | API | XML | Protocols Section 4.4.14, ERCOT Day-Ahead Ancillary Services Procurement Process |
| QSE Present Resource Plan | Unit Availability Status | Generation Planning, AS Verification | QSE | ERCOT | Daily @ 1600, then as needed | API | XML | Protocols Section 4.4.15, QSE Resource Plans |
|  | Unit Planned Net Hourly Generation MW | Generation Planning, AS Verification | QSE | ERCOT | Daily @ 1600, then as needed | API | XML | Protocols Section 4.4.15, QSE Resource Plans |
|  | Unit Planned High Net Hourly Operating Limit MW | Generation Planning, AS Verification | QSE | ERCOT | Daily @ 16000, then as needed | API | XML | Protocols Section 4.4.15, QSE Resource |
|  | Unit Planned Low Net Hourly Operating Limit MW | Generation Planning, AS Verification | QSE | ERCOT | Daily @ 1600, then as needed | API | XML | Protocols Section 4.4.15, QSE Resource Plans |
|  | Load acting as a Resource | Generation Planning, AS Verification | QSE | ERCOT | Daily @ 1600, then as needed | API | XML | Protocols Section 4.4.15, QSE Resource Plans |
|  | Notification to QSE for insufficient resources | Generation Planning, AS Verification | ERCOT | QSE | Daily by 1600 | API | XML | Protocols Section 4.1.1, QSE Resource Plans |
| Procure Replacement Reserve Service | Unit-Specific Replacement Reserve Service (RPRS) Bids | QSEs may submit Replacement Reserve Service (RPRS) Bids | QSE | ERCOT | Daily by 1600, then as needed | API | XML | Protocols Section 4.4.16, ERCOT Receipt of Replacement Reserve Service Bids |
|  | Resource Specific Premiums | QSEs may submit hourly Resource specific premiums | QSE | ERCOT | Daily by 1430, then as needed | API | XML | Protocols Section 4.5.3, ERCOT Receipt of Resource Specific Premiums for Operational Congestion Management |
|  | Procurement of Replacement Reserve | ERCOT purchase RPRS | ERCOT | QSE | Daily by 1800 | API | XML | Protocols Section 4.4.17, ERCOT Procurement of Replacement Reserve Service As Needed |
|  | Adjustments to schedules of Reliability Must-Run (RMR) resources | Adjustments to the QSE's schedules | ERCOT | QSE | Demand | API | XML | Protocols Section 4.5.11 , ERCOT Deployment of Reliability Must-Run Generators |
| ADJUSTMENT PERIOD |  |  |  |  |  |  |  |  |
|  |  | QSE's can make schedule adjustments and ERCOT can request additional bids. |  |  | Time T is the start of the Operating Period |  |  | The Adjustment Period (AP) begins following the close of the Day-Ahead market and continues until one (1) hour prior to the beginning of the Operating Hour. |
| Adjustment Period Schedule Changes | Submit or change Energy Schedule and Ancillary Services Schedules | Adjustment Period Scheduling Process | QSE | ERCOT | T minus 60 minutes | API | XML | Protocols Section 4.5.1, Receipt of Adjustment Period Schedule Changes |
|  | Submit, change, or remove Balancing Energy Service Up and Down Bids | Adjustment Period Scheduling Process | QSE | ERCOT | T minus 60 minutes | API | XML | Protocols Section 4.5.1, Receipt of Adjustment Period Schedule Changes |
|  | Submit, change, or remove RPRS Bids | Adjustment Period Scheduling Process | QSE | ERCOT | T minus 60 minutes | API | XML | Protocols Section 4.5.1, Receipt of Adjustment Period Schedule Changes |
|  | Require mandatory Balancing Energy Service Down Bid Curves | Adjustment Period Scheduling Process | ERCOT | QSE | T minus 60 minutes | API | XML | Protocols Section 4.5.2, Receipt of QSE's Balancing Energy Bid Curves |
|  | Submit Balancing Energy Service Up and Down Bid Curves | Adjustment Period Scheduling Process | QSE | ERCOT | T minus 60 minutes | API | XML | Protocols Section 4.5.2, Receipt of QSE's Balancing Energy Bid Curves |
|  | Announce need to procure RPRS | Procure Submitted Bids | ERCOT | QSE | T minus 60 minutes | API | XML | Protocols Section 4.5.6, ERCOT Notice of Need to Procure Replacement Reserve Service Resources |
|  | Announce need to procure additional Ancillary Services | Procure Submitted Bids | ERCOT | QSE | T minus 60 minutes | API | XML | Protocols Section 4.5.8, ERCOT Notice of Need to Procure Additional Ancillary Services |
|  | QSE Update their Resource Plan | Update prior to close of the Adjustment Period | QSE | ERCOT | T minus 60 minutes | API | XML | Protocols Section 4.5.10, Updated Resource Plans |
|  | QSE Update their Balanced Schedules | Adjustment Period Scheduling Process | QSE | ERCOT | T | API | XML | Protocols Section 4.5.6 & 4.5.8, Updated Balanced Schedules |
|  | QSE Resubmit Corrected Balanced Schedule | Adjustment Period Scheduling Process | QSE | ERCOT | T plus 15 minutes | API | XML | Protocols Section 4.5.6 & 4.5.8, Corrected Balanced Schedule |
|  | Procure RPRS | ERCOT purchase RPRS | ERCOT | QSE | T plus 30 minutes | API | XML | Protocols Section 4.5.6, |
|  | Procure additional Ancillary Services | ERCOT purchase additional ancillary service | ERCOT | QSE | T plus 30 minutes | API | XML | Protocols Section 4.5.8, |
| OPERATING PERIOD |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | DNP 3.0 protocol will be used for new ports to RTUs or SCADA systems. |
| FCS Inputs | Frequency | Real-Time Monitoring and Control | ERCOT/QSE | ERCOT | 2 sec | RTU | DNP 3.0 | Protocols Section 6.10.5, QSE Real Power Performance Criteria |
| Unit Monitoring | Generating Unit MW | Real-Time Monitoring & Security Analysis | QSE | ERCOT | 2 sec | RTU | DNP 3.0 | Protocols Section 6.5.1.1, Requirements for Operating Period Data for System Reliability and Ancillary Service Provision Net Generation is preferred. If gross MW is supplied, aux load should also be provided. |
|  | Generating Unit Mvar | Real-Time Monitoring & Security Analysis | QSE | ERCOT | 10 sec | RTU /ICCP | DNP 3.0 | Protocols Section 6.5.1.1, Requirements for Operating Period Data for System Reliability and Ancillary Service Provision Net Generation is preferred. If gross MVar is supplied, aux load should also be provided. |
|  | Private Network Net Interchange to ERCOT | Real-Time Monitoring & Security Analysis | QSE | ERCOT | 2 Sec | RTU | DNP 3.0 | For private networks, the net interchange shall be provided along with gross MW and MVar per generating unit. |
|  | Private Network Net Interchange High Limit | Real-Time Monitoring & Security Analysis | QSE | ERCOT | 10 sec | RTU/ ICCP | DNP 3.0 | For private networks, the high operating limit will reflect the maximum generation available at the point of interconnection to ERCOT. |
|  | Private Network Net Interchange Low Limit | Real-Time Monitoring & Security Analysis | QSE | ERCOT | 10 sec | RTU/ ICCP | DNP 3.0 | For private networks, the low operating limit will reflect the minimum generation available at the point of interconnection to ERCOT. |
|  | Status of switching devices in the plant switchyard not monitored by the TDSP affecting flows on the ERCOT System | Real-Time Monitoring & Security Analysis | QSE | ERCOT | 10 sec | RTU/ ICCP | DNP 3.0 | Protocols Section 6.5.1.1, Requirements for Operating Period Data for System Reliability and Ancillary Service Provision |
|  | Generating Unit Breaker Status | Real-Time Monitoring & Security Analysis | QSE | ERCOT | 10 sec | RTU/ ICCP | DNP 3.0 | Protocols Section 6.5.1.1, Requirements for Operating Period Data for System Reliability and Ancillary Service Provision |
|  | Generating Unit High Operating Limit | Real-Time Monitoring & Security Analysis | QSE | ERCOT | 10 sec | RTU/ ICCP | DNP 3.0 | Protocols Section 6.5.1.1, Requirements for Operating Period Data for System Reliability and Ancillary Service Provision |
|  | Generating Unit Low Operating Limit | Real-Time Monitoring & Security Analysis | QSE | ERCOT | 10 sec | RTU/ ICCP | DNP 3.0 | Protocols Section 6.5.1.1, Requirements for Operating Period Data for System Reliability and Ancillary Service Provision |
| NOTE: perating Period data from QSE units can be made available to the PGCs host TDSP on request. |  |  |  |  |  |  |  |  |
|  | Load used as a Resource MW | Real-Time Monitoring | QSE | ERCOT | 2 sec | RTU | DNP 3.0 | Protocols Section 6.5.1.1, Requirements for Operating Period Data for System Reliability and Ancillary Service Provision |
|  | Load Resource Breaker Status | Real-Time Monitoring | QSE | ERCOT | 10 sec | RTU/ ICCP | DNP 3.0 | Protocols Section 6.5.1.1, Requirements for Operating Period Data for System Reliability and Ancillary Service Provision |
|  | Load Resource (providing Responsive Reserve) High-Set Underfrequency Relay Status | Real-Time Monitoring | QSE | ERCOT | 10 sec | RTU/ ICCP | DNP 3.0 | Protocols Section 6.5.1.1, Requirements for Operating Period Data for System Reliability and Ancillary Service Provision |
|  | QSE Frequency Bias | Real-Time Monitoring | QSE | ERCOT | 2 sec | RTU | DNP 3.0 | Protocols Section 6.5.1.1 Frequency Bias of Portfolio Generation under QSE Operation |
|  | Dynamic Resource Power Schedules | Real-Time Monitoring | QSE | ERCOT | 2 sec | RTU | DNP 3.0 | Protocols Sections 4.9 Implementation Principles for Dynamic Load Schedules and 6.10.4.3 - Schedule Control Error |
|  | SCE | Real-Time Monitoring and Control (control only for regulation providers) | QSE | ERCOT | 2 sec | RTU | DNP 3.0 | Feedback for QSE regulation calculation. Protocols Section 6.10.5, QSE Real Power Performance Criteria |
|  | Regulation Feedback (loop-back) | Real-Time Monitoring | QSE | ERCOT | 2 sec | RTU | DNP 3.0 | Protocols Section 6.5.1.1 Requirement for Operating Period Data for System Reliability and Ancillary Service Provision & 6.7.2(8), Regulation Service - Feedback the amount of RGS power (MW) being provided each control cycle |
|  | Responsive Reserve Availability MW | Real-Time Monitoring | QSE | ERCOT | 10 sec | RTU/ ICCP | DNP 3.0 | Feedback to Responsive Reserve Deployment. Protocols Section 6.7.3 (6), Deployment of Responsive Reserve Service |
|  | Responsive Reserve Deployment MW | Real-Time Monitoring | QSE | ERCOT | 10 sec | RTU/ ICCP | DNP 3.0 | Feedback to Responsive Reserve Deployment. Protocols Section 6.7.3 (6), Deployment of Responsive Reserve Service |
|  | Non-Spinning Reserve Availability MW | Real-Time Monitoring | QSE | ERCOT | 10 sec | RTU/ ICCP | DNP 3.0 | Feedback to Non-Spinning Reserve Deployment. Protocols Section 6.7.4 (7), Deployment of Non-Spinning Reserve Service |
|  | Non-Spinning Reserve Deployment MW | Real-Time Monitoring | QSE | ERCOT | 10 sec | RTU/ ICCP | DNP 3.0 | Feedback to Non-Spinning Reserve Deployment. Protocols Section 6.7.4 (7), Deployment of Non-Spinning Reserve Service |
| Deploy Ancillary Services | Instructed Regulation Up / Down MW | FCS Instruction | ERCOT | QSE | 4 sec | RTU | DNP 3.0 | Protocols Section 6.5.1.1, Requirement for Operating Period Data for System Reliability and Ancillary Service Provision & 6.7.2,(1) Regulation Service |
|  | Instructed Responsive Reserve MW | FCS Instruction | ERCOT | QSE | 4 sec | RTU | DNP 3.0 | Protocols Section 6.5.1.1, Requirement for Operating Period Data for System Reliability and Ancillary Service Provision & 6.7.3 (1), Responsive Reserve Service |
|  | SCE | Performance Monitoring | ERCOT | QSE | 10 sec | RTU | DNP 3.0 | SCE Comparison for real-time monitoring and analysis by the ERCOT and QSE. Protocols Section 6.10.4.4, Schedule Control Error |
|  | Governor Response | Monitoring | ERCOT | QSE | 10 sec | RTU | DNP 3.0 | ERCOT calculated governor response from QSE frequency bias. Protocols Section 6.10.4.4, Schedule Control Error |
|  | Generating Unit Governor Response | Real-Time Monitoring | ERCOT | QSE | 10 sec. | RTU | DNP 3.0 | Protocols Section 6.5.1.1 Requirements for Operating Period Data for System Reliability and Ancillary Service Provision. |
| FCS Control Instructions | Instructed Non-Spinning Reserve MW | Instruction | ERCOT | QSE | Every 15 minutes | API | XML | Protocols Section 6.7.4(6), Non-Spinning Reserve Service |
|  | Instructed Balancing Energy MW (Up / Down) | Instruction | ERCOT | QSE | Every 15 minutes with 10 minutes notice | API | XML | Protocols Section 6.5.2, & 6.7.1.1(8) Balancing Energy Service |
|  | Unit Automatic Voltage Regulator Status | Real Time Monitoring | QSE | ERCOT | 10 sec | RTU/ ICCP | DNP 3.0 |  |
|  | Unit High Side Bus Voltage kV | Real-Time Monitoring | QSE | ERCOT | 10 sec | RTU/ ICCP | DNP 3.0 | Protocols Section 6.5.7, Voltage Support Service, May be supplied by the TDSP. Low Side with appropriate transformer model may be substituted. |
|  | Bus Voltage at Private Network connection to ERCOT | Real-Time Monitoring | QSE | ERCOT | 10 sec | RTU | DNP 3.0 | This voltage may be supplied by the TDSP. |
| Reliability Instructions | Instructed Replacement Reserve | Instruction | ERCOT | QSE | As needed | API | XML | Protocols Section 6.5.6, Replacement Reserve Service |
|  | Instructed Voltage Support | Instruction | ERCOT | QSE | As needed | API | XML | Protocols Section 6.5.7, Voltage Support Service |
|  | Instructed Black Start | Instruction | ERCOT | QSE | As needed | API | XML | Protocols Section 6.5.8, Black Start Service |
|  | Instructed Reliability Must-Run | Instruction | ERCOT | QSE | As needed | API | XML | Protocols Section 6.5.9, Reliability Must-Run Service |
|  | Instructed Out-of-Merit Capacity | Instruction | ERCOT | QSE | As needed | API | XML | Protocols Section 6.5.10, Out-of-Merit Capacity and Out-of-Merit Energy Services |
|  | Instructed Out-of-Merit Energy | Instruction | ERCOT | QSE | As needed | API | XML | Protocols Section 6.5.10, Out-of-Merit Capacity and Out-of-Merit Energy Services |
| Security Analysis |  |  |  |  |  |  |  |  |
| Generation |  |  |  |  |  |  |  | Generating data is provided by QSEs as defined above under Operating Period Data |
| Bus |  |  |  |  |  |  |  |  |
|  | Bus Voltage kV | Real-Time Monitoring | TDSP | ERCOT | 10 sec | ICCP | Blocks 1&2 |  |
|  | Bus Frequency Hz | Real-Time Monitoring | TDSP | ERCOT | 10 sec | ICCP | Blocks 1&2 |  |
| Transformer |  |  |  |  |  |  |  |  |
|  | Transformer Flow MW | Real-Time Monitoring | TDSP | ERCOT | 10 sec | ICCP | Blocks 1&2 | Positive flow is into the transformer |
|  | Transformer Flow Mvar | Real-Time Monitoring | TDSP | ERCOT | 10 sec | ICCP | Blocks 1&2 | Positive flow is into the transformer |
|  | LTC Tap Position | Real-Time Monitoring | TDSP | ERCOT | 10 sec | ICCP | Blocks 1&2 |  |
|  | Transformer Status | Real-Time Monitoring | TDSP | ERCOT | 10 sec | ICCP | Blocks 1&2 | Used if the computer(s) have a Network Topology Processor |
| Line |  |  |  |  |  |  |  | Circuit Breaker data may be used instead of line data. |
|  | Line Flow MW | Real-Time Monitoring | TDSP | ERCOT | 10 sec | ICCP | Blocks 1&2 | Positive flow is out of the station |
|  | Line Flow Mvar | Real-Time Monitoring | TDSP | ERCOT | 10 sec | ICCP | Blocks 1&2 | Positive flow is out of the station |
|  | Circuit Status | Real-Time Monitoring | TDSP | ERCOT | 10 sec | ICCP | Blocks 1&2 | Used if the computer(s) have a Network Topology Processor |
| Shunt |  |  |  |  |  |  |  |  |
|  | Reactive Support from Shunt Mvar | Real-Time Monitoring | TDSP | ERCOT | 10 sec | ICCP | Blocks 1&2 | Positive for supplying VAR Negative for absorbing VAR |
|  | Bank Status | Real-Time Monitoring | TDSP | ERCOT | 10 sec | ICCP | Blocks 1&2 | Used if the computer(s) have a Network Topology Processor |
| Circuit Breaker |  |  |  |  |  |  |  | Includes: Circuit Breaker (CB), Line Switch (LS), and Disconnect Switch (DCS) (where applicable) Line data may be used instead of circuit breaker data. |
|  | CB MW flow | Real-Time Monitoring | TDSP | ERCOT | 10 sec | ICCP | Blocks 1&2 | Positive flow is from bus section to equipment (optional) |
|  | CB Mvar | Real-Time Monitoring | TDSP | ERCOT | 10 sec | ICCP | Blocks 1&2 | Positive flow is from bus section to equipment (optional) |
|  | Switch Position | Real-Time Monitoring | TDSP | ERCOT | 10 sec | ICCP | Blocks 1&2 |  |
| Load |  |  |  |  |  |  |  | Load metering is preferred from the high side of the transformation point of the substation distribution transformer. |
|  | Load in MW | Real-Time Monitoring | TDSP | ERCOT | 10 sec | ICCP | Blocks 1&2 | Negative for Load MW |
|  | Load in Mvar | Real-Time Monitoring | TDSP | ERCOT | 10 sec | ICCP | Blocks 1&2 | Negative for Load Mvar |
| DC Injection |  |  |  |  |  |  |  |  |
|  | DC Injection in MW | Real-Time Monitoring | TDSP | ERCOT | 10 sec | ICCP | Blocks 1&2 | Positive flow is out of the station |
|  | DC Injection in Mvar | Real-Time Monitoring | TDSP | ERCOT | 10 sec | ICCP | Blocks 1&2 | Positive flow is out of the station |
|  | DC Tie Status | Real-Time Monitoring | TDSP | ERCOT | 10 sec | ICCP | Blocks 1&2 | Used if the Computer(s) have a Network Topology Processor |
| Weather Zone Tie Lines | Line Flow MW | Real-Time Monitoring | TDSP | ERCOT | 10 sec | ICCP DNP 3.0 | Blocks 1&2 | TDSP’s responsible for supplying weather zone tie line data must provide a redudant path from their normal ICCP link. This second path may be a second ICCP association to ERCOT or an RTU or other device using DNP 3.0 protocol. |

NOTE:	Real-Time data for Security Analysis can be provided to TDSPs on request.

Private Network refers to generators with self-serve private load behind a single meter at the point of injection into the ERCOT grid.

LEGEND:

Supplied by/Received by

ERCOT - ERCOT Independent System Operator

QSE - Qualified Scheduling Entity

TDSP - Transmission, Distribution Service Provider

PGC - Power Generating Company

Mode of Communication

Web Portal - Online application available to market participants via the World Wide Web

TCH - Transaction Clearinghouse.  The mechanism used to send/receive EDI transactions

API - Programmatic API. A message protocol used to automate data exchange between ERCOT and market participants

ICCP - Inter-Control Center Communication Protocol. A standard protocol used to automate data exchange real-time control information between the ERCOT and participants

RTU - Remote Terminal Unit. Used to gather real-time control/monitoring information.

Format

EDI - Electronic Data Exchange format. EDI formats are specified by the Texas SET working group and are based on standard EDI transaction protocols.

XML - eXtensible Markup Language. XML is a self-describing meta language used to facilitate the exchange of data. XML will format requests and receive replies using the API.

CSV - Comma Separated Values. A generic file format where elements of data are separated by commas within a file.

Office Document - One of the common Microsoft Office file formats such as MS Word or MS Excel.