| OGRR Number | 121OGRR | OGRR Title | Fault Recording Equipment Maintenance and Testing |
| --- | --- | --- | --- |
| ###### Status |  | posted |  |
| Operating Guide Section Requiring Revision |  | Appendix B B.2.2.5 |  |
| Protocol Section Requiring Revision, if any. |  | ## N/A |  |
| Requested Resolution |  | ## Normal |  |
| Revision Description |  | Modify wording that allows manual and automatic triggers to count as a functional test as well as recorder event waveform analysis and verifications to count as calibration checks. |  |
| ###### Reason for Revision |  | This language was approved at the July 2001 SPWG meeting and proposed to ROS in August 2001. |  |
| ## Sponsor |  |  |  |
| Name |  | Jose Juan Martinez |  |
| E-mail Address |  | jjmartinez@cps-satx.com |  |
| Company |  | City Public Service |  |
| Company Address |  | 145 Navarro |  |
| Phone Number |  | (210)353-3556 |  |
| Fax Number |  | (210)353-4449 |  |
| ## Timeline |  |  |  |
| Date Received |  | 09/18/2002 |  |
| Date Posted |  | 09/20/2002 |  |
| Comments Due |  | 10/11/2002 |  |
| ROS Review Date |  |  |  |
| ROS Recommendation |  |  |  |
| Other Subcommittee Consideration |  |  |  |
| TAC Consideration |  |  |  |
| Board Consideration |  |  |  |

Proposed Operating Guide Language Revision

#### B.2.2.5	Maintenance and Testing Requirements

Facility Owners shall maintain and test their Fault recording equipment as follows:

- In accordance with the manufacturer’s recommendations.

- Calibration of the analog (waveform) channels shall be performed at installation and when records from the equipment indicate a calibration problem.  Calibration can be monitored through the analysis and correlation of fault records with system models and the records of other fault recorders in the area.

- Fault recording equipment must be operationally tested at least annually to ensure that the equipment is functional.  Acceptable tests are the production of a manually triggered record, automatic record production due to a power system disturbance, or responsiveness to remote polling / interrogation of the equipment via a communications channel.

| ## Other TAC Subcommittee Review |  |
| --- | --- |
| PRS Review Date |  |
| PRS Protocols Impact Decision |  |
| WMS Review Date |  |
| RMS Review Date |  |
| ## TAC Action |  |
| TAC Vote Date |  |
| TAC Proposed Implementation Date |  |
| TAC Vote Results |  |