| OGRR Number | 121OGRR | OGRR Title | Fault Recording Equipment Maintenance and Testing |
| --- | --- | --- | --- |
| Status | posted |
| Operating Guide Section Requiring Revision | Appendix B B.2.2.5 |
| Protocol Section Requiring Revision, if any. | N/A |
| Requested Resolution | Normal |
| Revision Description | Modify wording that allows manual and automatic triggers to count as a functional test as well as recorder event waveform analysis and verifications to count as calibration checks. |
| Reason for Revision | This language was approved at the July 2001 SPWG meeting and proposed to ROS in August 2001. |
| Sponsor |
| Name | Jose Juan Martinez |
| E-mail Address | jjmartinez@cps-satx.com |
| Company | City Public Service |
| Company Address | 145 Navarro |
| Phone Number | (210)353-3556 |
| Fax Number | (210)353-4449 |
| Timeline |
| Date Received | 09/18/2002 |
| Date Posted | 09/20/2002 |
| Comments Due | 10/11/2002 |
| ROS Review Date |  |
| ROS Recommendation |  |
| Other Subcommittee Consideration |  |
| TAC Consideration |  |
| Board Consideration |  |

Proposed Operating Guide Language Revision

#### B.2.2.5	Maintenance and Testing Requirements

Facility Owners shall maintain and test their Fault recording equipment as follows:

In accordance with the manufacturer’s recommendations.

Calibration of the analog (waveform) channels shall be performed at installation and when records from the equipment indicate a calibration problem.  Calibration can be monitored through the analysis and correlation of fault records with system models and the records of other fault recorders in the area.

Fault recording equipment must be operationally tested at least annually to ensure that the equipment is functional.  Acceptable tests are the production of a manually triggered record, automatic record production due to a power system disturbance, or responsiveness to remote polling / interrogation of the equipment via a communications channel.

| Other TAC Subcommittee Review |
| --- |
| PRS Review Date |  |
| PRS Protocols Impact Decision |  |
| WMS Review Date |  |
| RMS Review Date |  |
| TAC Action |
| TAC Vote Date |  |
| TAC Proposed Implementation Date |  |
| TAC Vote Results |  |