ERCOT Operations Report

@

ROS & OWG

For August 2002

Frequency control issues (High or Low Frequency) 59.9 > F > 60.1.

During the month of August five  low frequency and no high frequency occurrences were observed.  The highest frequency value was 60.092 on August 26th at 18:08 and the lowest was 58.88 on August 5th at 02:34.  Significant events resulting in frequency excursions are noted below.

- At  02:34 on 8/5 a unit carrying 600 MW tripped. Frequency deviated from 59.96 to 59.88  and recovered within 5 minutes.

- At 10:20 on 8/19 a unit carrying 560 MW tripped.  Frequency dipped to 59.862 and recovered within 5 minutes.

- At 21:04 on 8/19 Frequency dipped to 59.882 a unit carrying 550 MW tripped.  Frequency recovered to 60 HZ at 21:07.

- At 08:37 on 8/22 a unit carrying 770 MW tripped.  Frequency dipped to 59.826 and recovered within 5 minutes.

- At 09:13 on 8/24 the East DC tie tripped carrying 400 MW. Frequency dipped to 59.90.

Congestion Management Occurrences & Related Problems.

Major Computer Systems Problems/ Fixes.

8/22 22:37-23:25	MOI locked up from alarms.  Both market servers down caused by a known hardware problem.  Issued OCN Advisory on MIS.

New Procedures/ Forms/ Operations Bulletins.

8/14	Power Operations Bulletin 7 was issued describing enhancements to the Outage Scheduler.

Security Alert Stage/ Threatcon/ Related issues.

Threatcon LOW was maintained throughout August.

Describe each EECP Occurrence.

No EECP Occurrences.

Number of OCN, Alert, Energy Notice and Major Disturbances

Six OCN issued including three transmission alerts, loss of communication, loss of MOI and loss of a resource.  One Emergency Notification for reliability of the Rio-Grande Valley at 16:10 on 8/19.  An advisory was issued at 14:16 when the first-contingency limit was exceeded.

Major Weather Related Power System Problems

No significant weather related problems.

Significant Communication Problems

8/2  03:45	  Lost telemetry link with TXU and Tenaska.  SWB cable down for maintenance.

8/22 22:37-23:25	 MOI locked up from alarms.  Both market servers down caused by a known hardware   problem.  Issued OCN Advisory on MIS.

8/18  08:00-11:40 Portal out of service due to planned maintenance which did not go as planned.

Major system Voltage problems

No voltage problems reported during the month of August.

Blackout/Load Shed incidences

No load shed/blackout incidences within EROT.

ERCOT peak for last month (Date and Time)

8/26 17:00	Monthly peak of 55,957 MW was observed.

Update on new generation

Max temperature/ Minimum Temperature

8/26  17:00	101F recorded (Austin)

8/29  07:00	  66F recorded (Abilene)

New SPS & RAP’s

No new RAP/SAP posted.

Issues with ERCOT entities

Some entities claim that they no longer need to maintain responsive reserve service schedules if they are receiving unit specific constraint instructions.  ERCOT believes that they are obligated to maintain RRS capability to match schedules in order to be compensated.  If entities are incapable of maintaining this obligation, ERCOT may need to open additional markets.