ERCOT Operations Report

@

ROS & OWG

For October 2002

Frequency control issues (High or Low Frequency) 59.9 > F > 60.1.

| Time | Frequency |  |
| --- | --- | --- |
| 10/1/2002 15:18 | 59.8769989 | Large unit trip |
| 10/4/2002 5:12 | 59.88700104 |  |
| 10/5/2002 22:59 | 59.85599899 |  |
| 10/5/2002 23:05 | 60.10100174 | One QSE's SCE large positive. |
| 10/6/2002 13:24 | 59.88100052 | One QSE's SCE large negative |
| 10/7/2002 4:55 | 60.1629982 | Appears QSE's ramped in too early for interval. |
| 10/9/2002 17:03 | 60.18199921 |  |
| 10/9/2002 21:08 | 60.12099838 |  |
| 10/11/2002 5:46 | 59.89799881 | One QSE's SCE large negative. |
| 10/12/2002 21:08 | 60.11600113 |  |
| 10/13/2002 1:51 | 59.73300171 | Large unit trip. |
| 10/14/2002 21:10 | 60.16799927 |  |
| 10/15/2002 4:59 | 59.86999893 |  |
| 10/16/2002 5:03 | 59.89400101 |  |
| 10/17/2002 9:09 | 59.864254 |  |
| 10/18/2002 4:59 | 60.12200165 |  |
| 10/18/2002 21:02 | 59.88899994 |  |
| 10/18/2002 22:03 | 59.89199829 | One QSE's SCE large negative. |
| 10/20/2002 21:07 | 60.10100174 |  |
| 10/21/2002 14:31 | 59.87200165 |  |
| 10/22/2002 18:11 | 59.87799835 |  |
| 10/26/2002 21:09 | 60.12799835 |  |
| 10/27/2002 1:20 | 60.10200119 |  |
| 10/27/2002 22:11 | 60.11700058 |  |
| 10/28/2002 7:08 | 59.86899948 |  |
| 10/28/2002 20:09 | 59.83599854 | Unit tripped carrying 600 MW. |
| 10/28/2002 22:09 | 60.13399887 | One QSE's SCE large positive. |
| 10/30/2002 5:22 | 59.8769989 |  |
| 10/30/2002 17:14 | 59.74300003 | Large unit trip. |

## Congestion Management Occurrences & Related Problems

*Days of units purchased for some time in the area described.  Data taken form daily reports and is approximate.  For global overview purposes only.

Major Computer Systems Problems/ Fixes.

None Applicable

New Procedures/ Forms/ Operations Bulletins.

10/3	Power Operations Bulletin 8 ‘Load Shed Ratios assigned to Transmission Operators in ERCOT for shedding firm load during step 4 of EECP’ posted.

Security Alert Stage/ Threatcon/ Related issues.

Threatcon LOW throughout October.

Describe each EECP Occurrence.

10/6	15:30	EECP Advisory sent out due to UBES deficiency for ie 15:30-16:00.

OCN, Alert, Energy Notice and Major Disturbances

10/2	13:46		SMD K-7 warning.

10/2	17:46		OCN Wet weather/hurricane warning.

10/18	16:18 – 16:25	OCN issued to inform QSE’s ERCOT EMS system down, and no deployments

being sent.

Major Weather Related Power System Problems

none

Significant Communication Problems

10/1	The 04:30 deployments went out but no one received them. We held the 04:15 deployments until further notice. Help Desk noted and sent out a Communication Advisory.

10/24	The forecasted Ancillary Services for next month were not posted on the 20th, so they were posted 10/24.

10/30   	18:20-19:40	Manually dispatch due to failure of both MOI systems.

Major system Voltage problems

None

Blackout/Load Shed incidences

None

ERCOT peak for last month (Unofficial)

10/3 12:40 49,073

Update on new generation

10/16/2002   00:01  Corpus Christie Energy Center commercially operational.

Max / Min Temperature

Max:	94	Houston 	10/3 & 10/4	15:00

Min	39	Abilene		10/31		06:00 – 10:00

New SPS & RAP’s

None

Issues with ERCOT entities

Thursday 10/31, Shifted primary operations to the Taylor facility.