| OGRR Number | 118-OGRR | OGRR Title | Black Start |
| --- | --- | --- | --- |
| ###### Date |  | September 26, 2002 |  |
| Operating Guide Section Requiring Revision |  | 4.6 |  |
| Revision Description |  | Revision updates language and adds consistency to the Black Start Section of Part 4: Emergency Operation. Additions include: Transmission Operator Black Start Plan requirements and the Detailed Black Start Information found in Attachment A. References to the Pilot Program were removed, and a distinction was made between the Black Start responsibilities of Transmission Operators and TDSPs. |  |
| ###### Reason for Revision |  | The intent of this revision is to improve consistency between the Operating Guides and the Annual Black Start Plan. The Black Start section of the Operating Guide is meant to contain general Black Start instruction, whereas the Annual Black Start Plan contains the specific plan for Black Start recovery. |  |
| ## Sponsor |  |  |  |
| Name |  | OGRTF |  |
| E-mail Address |  | ogrtf@ercot.com |  |
| Company |  |  |  |
| Company Address |  |  |  |
| Phone Number |  |  |  |
| Fax Number |  |  |  |

Proposed Operating Guide Language Revision

## 4.6	Black Start

This section provides general philosophies to be followed in the event of a partial or complete collapse of the ERCOT system. Timely implementation of a restoration plan compiled according to this guide should facilitate coordination between ERCOT, QSEs, PGCs, and TOs and ensure restoration of service to the ERCOT System at the earliest possible time.  Those QSEs representing contracted Black Start Units will provide ERCOT with the individual plant start-up procedures for coordination of their activities with those of the appropriate TO.

Pre-established plans and procedures cannot foresee all the possible combinations of system problems that may occur after a major failure.  It is then the responsibility of ERCOT to restore the system to normal, applying the principles, strategies, and priorities outlined in this section and in The ERCOT Black Start Plan.

Reference: Protocols, Section 22, Black Start Agreement,

If the ERCOT Transmission Grid at the Black Start Resource becomes deenergized and if Participant cannot communicate with either ERCOT or the TDSP serving the Black Start Resource, then Participant shall follow the procedures specified for the Black Start Resource under ERCOT’s Black Start Plan in the Operating Guides, but Participant shall not commence delivering electric energy into the ERCOT System without specific instructions to do so from either ERCOT or the TDSP serving the Black Start Resource.

“Available” means, with respect to a given hour, that Participant has declared, in its Availability Plan, that the Black Start Resource is able to black start without a connection to the ERCOT Transmission Grid, provided that the Black Start Resource is not “Available” if it has failed a Black Start Test, as defined in the Operating Guides, or has failed to black start when required to black start under this Agreement, and it has not since passed a subsequent Black Start Test.

4.6.1	Principles

In order to minimize the time required, ERCOT will coordinate the restoration utilizing the principles, strategies, and priorities outlined in this guide.

ERCOT shall establish and maintain a system black start capability plan that shall be coordinated, as appropriate, with the black start capability plans of neighboring Regions. Documentation of system black start capability plans shall be provided to NERC on request. (NERC Planning Standards)

Each contracted Black Start Unit and each QSE with contracted Black Start Unit(s) will have readily accessible and sufficiently detailed current operating procedures to assist in an orderly recovery.

Mutual assistance and cooperation will be essential during the restoration.  Deliberate, careful action by each QSE, TO, and PGC is necessary to minimize the length of time required for restoration and to avoid the reoccurrence of a partial or complete collapse.

Throughout the restoration, recovery will depend on ERCOT receiving an accurate assessment of  system conditions and status from each QSE, TO, and PGC throughout the restoration. Adequate and reliable communications must be available within the ERCOT System. During Black Start Recovery, communication restrictions are lifted to enable the sharing of only that information that pertains to reliability including status information and recovery activities.

### 4.6.2 	Strategies

In the event of a partial or complete system blackout, immediate steps must be taken to return the interconnected network to normal as quickly as possible.

Each TO shall immediately initiate its portion of the Black Start procedure and attempt to establish contact with ERCOT.  If communications with ERCOT are unavailable the TO shall immediately establish communications with its interconnected Black Start Unit(s) and the Black Start Unit’s(s’) QSE.

Each QSE with representing Black Start Units should initiate communications with its Black Start Units and immediately notify ERCOT and the appropriate TO of their condition and status.

Available Black Start Units should immediately start their isolation and startup procedures and attempt to establish communications with the local TO.

As generating and transmission capabilities become available, systematic restoration of ERCOT load with respect to priorities should begin in accordance with the local TO Black Start Plans, taking care to balance load and generating capability while maintaining an acceptable frequency.

Appropriate voltage levels and reactive control must be maintained during the restoration.  Consideration should be given to connecting islands at locations having communications, frequency control, voltage control, synchronization facilities, and adequate transmission capacity.  ERCOT will coordinate the return to full Automatic Generation Control in the interconnection.

### 4.6.3	Priorities

Priorities for an ERCOT system restart are listed below:

- Secure and/or stabilize generating units where necessary.

- Prepare transmission corridors as necessary to support restoration.

- Assess ERCOT system condition, and available communication facilities.

- Restore and maintain communication facilities to the extent possible.

- Bring units with contracted black start capability on-line.

- Provide service to critical facilities:

- Provide station service for nuclear generating facilities.

- Provide critical power to as many power plants as possible to prevent equipment damage.

- Secure or provide startup power for generating plants that do not have black start capability.

- Supply station service to critical substations where necessary.

- Connect islands at designated synchronization points taking care to avoid recurrence of a partial or complete system collapse.

- Restore service to critical loads such as:

- Military facilities.

- Facilities necessary to restore the electric utility system, including fuel sources.

- Law enforcement organizations and facilities affecting public health.

- Public communication facilities.

- Restore service to the remaining customers.  Attention should be given to restoring feeders with under-frequency relay protection.

### Responsibilities

| OPERATOR | ACTION |
| --- | --- |
| ERCOT | - Shall maintain a Black Start Plan in accordance with NERC Policies. - Coordinate and approve planned outage schedule for contracted Black Start Units. - Train QSE, TO, PGC, and market participant personnel in the implementation and use of the Black Start Plan. - In the event of an ERCOT system collapse, ERCOT will: - Maintain continuous surveillance of the status of the ERCOT system - Act as a central information collection and dissemination point for the region - Coordinate reconnection of transmission - Direct assistance for QSEs, TOs, PGCs, and Market Participants. - Direct the distribution of reserve. - Coordinate the return of the ERCOT system to Automatic Generation Control. |
| Transmission Operator | - Shall maintain a local Black Start Plan which coordinates with the ERCOT Black Start Plan - In event of an ERCOT or wide area blackout: - Shall communicate with local Black Start Units and the Black Start Unit’s QSE - Coordinate switching to next start units and local load - Shall implement its local Black Start Plan - Shall follow the direction of ERCOT on behalf of represented TDSPs. - Shall act as the regional ERCOT representative in coordinating interconnection of units - Shall follow the direction of ERCOT for reconnection of islands. |
| QSEs, PGCs, and Market Participants | - Shall use the ERCOT and local TO Black Start Plan - Verify that associated personnel are proficient in its implementation and use. - In the event of an ERCOT system collapse, the QSEs, PGCs, and Market Participants will: - Take immediate steps to initiate the local Black Start Plan. - Supply ERCOT and/or the local TO with information on the status of generation, fuel, transmission, and communication facilities. - Follow the direction of the local TO or ERCOT in picking up local load and starting next units. - Provide available assistance as directed by ERCOT or the local TO. |

### Comment:  Moved to Attachment A.4.

### Attachment A provides a detailed and specific Black Start information guide.  Interested parties should use this information for technical reference material, Black Start Testing, development of Black Start Plans, and training of personnel.

###### Comment:  Attachment A below has been replaced by Appendix 1 found in the 2002 Black Start Plan.

###### Attachment A:	Detailed Black Start Information

- The following attachment provides detailed and specific information to be used in conjunction with the ERCOT Black Start Plan.  Each TO, QSE, and Generator should use this information for technical reference, development of Black Start Plans, and training of personnel.

- A.1	CONSIDERATIONS FOR SYSTEM RESTORATION

- a.	Determining System Status

If a Generator or TO loses voltage on all busses and incoming transmission lines, then operators should assume there is a system wide blackout.  The TO should immediately notify ERCOT if possible.  Contracted Black Start units should implement Black Start procedures and establish contact with their TO.  Other Generators should contact their QSE and then wait for instructions from the TO.  If possible, ERCOT will update TOs and QSEs concerning ERCOT system status by use of the hotline.

- It is expected that if communication with ERCOT is not possible TOs will evaluate system conditions and proceed independently with their Black Start Plans if needed.

- Priority should be given to determining the status of nuclear power plant facilities and switchyards in order to re-establish offsite power supply.

- System status conditions to be surveyed include but are not limited to:

- Areas of the system that are de-energized.

- Areas of the system that are functioning.

- Amount of generating reserve available in functioning areas.

- Power plant availability and time required to restart.

- Status of transmission breakers and sectionalizing equipment along critical transmission corridors, and at power plants.

- Status of transmission breakers and sectionalizing equipment at tie points to other areas.

- Status of fuel supply from external suppliers.

- Under-frequency relay operation.

- Relay flags associated with circuits tripped by protective relays.

- b.	Verifying Communications

Reliable communications will be the key to a safe and timely restoration following a collapse within the ERCOT system.  As part of the initial assessment after a partial or complete system collapse, communication facilities should be tested and verified.  It is possible, especially in case of a total ERCOT collapse, that communications with out-of-state QSEs may not be possible.  It is therefore critical that TOs and Generators located within their transmission system be able to communicate directly during these times.

- The ERCOT System Operators should:

- Verify or establish communication paths with TOs.

- Verify or establish communications paths with QSEs.

- Verify integrity of ERCOT hotline.

- Periodically disseminate information to TOs and QSEs.

- The TO operators should:

- Contact ERCOT in order to report status.

- Establish contact with Contracted Black Start Units and the Black Start Units’ QSE

- Initiate Black Start Plan

- Establish communication paths with other plants necessary to the restoration of the system in their area.

#### The QSE should:

- Contact ERCOT to report status of Generators within ERCOT

- Assist TOs as required.

- Ensure Generators are prepared to receive and follow instructions directly from the TO to which they are connected.

- Should problems be encountered with any of the primary communication facilities, alternate facilities should be established and this information conveyed to appropriate personnel.

- Communications will be vital to an orderly recovery.  To keep communication facilities available, operating personnel should ensure that conversations are concise and effective.

- c.	Preparing for System Restoration

- Orderly restoration will usually require sectionalizing the de-energized parts of the system into smaller, manageable blocks before they are energized.

- The sectionalizing process should usually address the following objectives:

  - Priority should be given to restoring offsite power to nuclear power plants.

  - Make blocks of load to be energized as small as possible to minimize the problems of cold load pickup.

  - Operators should verify that their switching orders as well as any standing emergency switching orders have been completed.

- d.	Bringing Up Plants

- First priority should be given to preventing damage to power plant equipment and to restoring offsite power to nuclear power plants.  Secondly, attention should be given to preparing units that can come on line most rapidly.  All operators should remember that large steam plants will need an outlet for the minimum generation requirement soon after coming on line.

- Plants with contracted Black Start capability have procedures to begin the process of bringing their units back up when the switchyard and all incoming transmission lines are de-energized.  The plant should not synchronize or pickup load without communicating with the TO to which they are connected unless their local Black Start Plan instructs them to do so.

- Plants without Black Start capability should have a Black Start Plan in place to begin preparing the plant to be energized from an external line.  When the TO has energized the plant switchyard it will contact the Generator directly and the QSE as soon as practical.  The TO will coordinate the starting of large motors, bringing the plant on line, and synchronization of the plant with the rest of the TO island.

- Some combustion and steam turbines may have relatively high set under-frequency and low over-frequency relays that could cause unit trips in the initial stages of recovery. Plant operators will be controlling system frequency during this period and must keep it between trip points.  It is preferable to use the units with lowest under-speed trip for initial restoration.

- Automatic voltage regulators should be placed in service as soon as practical after bringing units on line and should remain in service to improve machine stability.

- As soon as possible, after bringing a unit on line, automatic governor controls should be placed in the "automatic" position to insure instantaneous governor response to changes in load.

- e.	Picking Up Lines

- Ties between nearby power plants should be established as soon as possible. Priority should be given to restoring at least one circuit to nuclear power plants to provide offsite power for safe shutdown.

- A line should be energized from the strongest electrical source.  Switching devices on all substation or transmission capacitor banks along the line should be open unless needed for voltage control.

- Energizing transmission auto-transformers (345/138 kV, 138/69 kV) and shunt reactors at plants will allow plant operators to increase field current on the Generator to increase stability.  Also, this reactive current will help keep transmission voltages from becoming excessive.

- Caution should be exercised in the use of 345 kV transmission system.  Because of high values of line charging, energizing one of these circuits with little or no load can produce excessive voltage and can damage substation equipment  (Note: 345KV lines require approximately 1 MVAR/mile of line charging while 138KV lines require 0.3 MVAR/mile).

- TO Operators should exercise care when energizing transmission lines, so that they do not close a breaker into a fault.  TO Operators should be aware of any transmission lines that tripped while the system was going down and have field personnel check the relay flags before energizing the line.

- Ferroresonance may occur while energizing a line or while picking up a transformer from an unloaded line.  TO Operators should be on guard for unusually high and sustained voltages during such switching.  345 kV lines may be highly susceptible to this phenomenon and their use should be minimized in the early stages of restoration.

- Impedance relays that do not have out of step blocking may trip lines due to power swings during restoration (a good indication that the line tripped due to excessive power swings rather than a fault is the existence of impedance relay flags and no ground flags).

- f.	Picking Up Load

- In general, 69 kV and 138 kV lines along with radial 345 kV lines to autotransformers may be used to energize load.  When energizing a 345 kV circuit and autotransformer combination, both the line and transformer should be energized at the same time to avoid the problem of excessive voltage.  The more lightly loaded a unit is, the less load increment it can safely pick up.

- Cold load pickup can involve inrush currents of 10 or more times the normal load current depending on the nature of the load being picked up.  This will generally decay to about two times normal load current in two to four seconds and remain at a level of 150 to 200% of pre-shutdown levels for as long as thirty minutes.

- Priority should be given to restoring offsite power to nuclear power plants.  As critical and priority loads are restored, consideration should be given to restoration of loads controlled by under-frequency relays.

- When energizing load, the TO Operators must be in close contact with the Generator in order that excessive load is not picked up on a unit in one operation.  Generally, pick up no more than 5% of the total generating capability in an island in a single step.  If load is picked up in blocks that are too large, then the current inrush may operate over current relays that trip the loads off the system again.  There should be sufficient time between switching operations to allow the units to recover from the sudden increase in load.

- Exercise caution when loading a single unit to more than 50% of its control range until additional units have been brought back on-line in that island. Generally, no unit should be loaded to more than 80% of its normal rating until system conditions return to normal.

- Since each plant may be operating independently, plant operators will have to monitor and adjust their unit's voltage and frequency.  Frequency should be kept above 59.8 Hz and as close as possible to 60 Hz.  Voltage should be kept as close as possible to normal schedules.  As more units are brought up and more load is added, the voltage and frequency will tend to stabilize.

- Residential and commercial load will most likely be easier to pick up and maintain than industrial loads.  This is due to the large fluctuation possible with industrial loads.

- Exercise caution when re-energizing capacitor banks after load has been picked up.  The change in system voltage that occurs will be much larger than normal because of the reduced system fault duty.

- g.	Synchronizing Between Islands

- TOs should have field personnel in area islands to check breakers at each end of the line to insure they are open regardless of supervisory indication.  The area with the largest amount of generation on-line should energize the line first.

- Where available, field personnel should synchronize and close the tie breakers at the point of interconnection.  If there is a sufficient frequency difference that the islands cannot be synchronized, the island with the least generation on-line should adjust its frequency to achieve synchronization.

- When synchronizing, both the phase angle across the breaker, and the voltage on each side of the breaker should be measured.  If possible, the phase rotation should be stopped and the phase angle reduced to 10 degrees or less before closing the breakers.

- In general lines should not be loaded to more than 50% of thermal rating until multiple tie paths have been established.  Additional ties should be closed as soon as possible.

A.2	ERCOT COORDINATION

- During the initial stages of the restoration ERCOT will coordinate the Black Start restoration effort by monitoring the implementation of each TO’s Black Start Plan, providing system status information, and facilitating communication between market participants.  ERCOT will also monitor the changes in generation conditions, restoration of transmission lines, and any load that is re-energized.  The ERCOT hotline will periodically be used to communicate simultaneously with the market participants on a periodic basis assuming communication is possible.

System status conditions, which should be surveyed, include but are not limited to:

- Communication Facilities

- Transmission System

- Generating System

- Fuel Supplies

- Any significant conditions which might affect restoration

ERCOT System Operators should be sure that each TO and Generator is successfully implementing its Black Start Plan.  ERCOT System Operators will direct mutual assistance by utilizing the Black Start map and contacting the Market Participants most able to provide the assistance.

Before synchronization of inter-company islands ERCOT will designate what entity is responsible for frequency control in the combined islands.  Initially this may be a single plant.  As the restoration effort progresses, ERCOT will work to combine islands in such a way as to restore frequency control of one of the QSEs.  As inter-company islands are synchronized ERCOT will approve the addition of generation and load to the system.  No additions should be made without that approval.

A.3	Considerations For Black Start Testing

As prescribed by the ERCOT Protocols, testing must be performed to qualify black start resources.

ERCOT shall maintain a record of black start generators within ERCOT and update such records on an annual basis.  The record shall include the name, location, MW capability, type of unit, date of test, and starting method of each Black Start  Unit.  (NERC Planning Standards) A Black Start Unit Test Results Form is available from ERCOT.

The owner or operator of each Black Start  Unit shall demonstrate through the testing procedures outlined in Protocols Section 6.10.3.6, that the unit can perform its intended functions as required in the system restoration plan.  ERCOT may also order random simulation or testing of black start capabilities as described in Protocols Section 6.5.8. Documentation of the analysis shall be provided to NERC on request.  (NERC Planning Standards)

The results of the testing of the startup and operation of each Black Start  Unit shall be documented and provided to NERC on request.  (NERC Planning Standards)

### A.4	Criteria for ERCOT and Transmission Operator Black Start Plans

ERCOT will maintain a Black Start Plan that is consistent with this Guide.  All plans and procedures shall be readily available to the System Operators and copies of appropriate plans shall be provided to the QSEs, TOs, and PGCs..

ERCOT System Operators should review these documents on a regular basis.  It is suggested that the ERCOT Black Start Plan include the following elements:

- Strategies and philosophies for ERCOT restart.

- Identification of the relationships and responsibilities of the QSEs, TOs, and market participant's personnel necessary to the restoration.

- Identification of Black Start resources including:

- Unit resources.

- Transmission resources.

- Communication resources.

- Fuel resources.

- Mutual assistance arrangements.

- Contingency plans for failed resources.

- Identification of critical load requirements

- Identification of special equipment requirements

- General instructions and guidelines for ERCOT System Operators, PGC, QSE, and TO operators and their respective communications personnel.

- Procedures for Public Notification.

- Procedures for return to Market Operations.

When incorporated into the general instructions and guidelines for the ERCOT System Operators, the elements listed above will supply a broad background of information available for use to effectively recover from a major ERCOT System collapse.  These elements will also help to identify common problems facing the ERCOT System during restoration.  It is essential that all appropriate personnel be familiar with these plans and procedures so that the ERCOT System can be restored to normal as quickly as possible.

Transmission Operators shall maintain a local Black Start Plan that is coordinated with the ERCOT Black Start Plan, but provides additional local detail. The TO Black Start Plan should include sections on the Black Start scope, communication process, and operations as outlined below.

A SCOPE section shall provide the main objectives, responsibilities, and expected actions of the TO and other market entities in the event of system blackout. This section should address at least the following items:

a.	Roles and Responsibilities

  - TO plan should identify its role as well as those of generating resources and ERCOT in the case of a blackout.

b.	Identifying the blackout event

  - TO plan should clearly state how a blackout event will be recognized and what actions the TO operator needs to initiate restoration as well as what actions should be expected from ERCOT and other market participants.

c.	Assessing and verifying communication capabilities

  - TO plan should include a procedure for assessing communication capabilities and a plan for dealing with failures of various systems.

d.	Transferring control away from ERCOT

  - In the event of a blackout, the TO will have ERCOT’s authority to bring units on line and energize load.  The TO should note that it may not be possible for ERCOT to communicate this transfer of authority and that the transfer can be assumed once a blackout condition has been identified.

e.	Starting the Black Start Units

  - The TO plan should primarily rely on contracted Black Start Units in restoring the system.  However, the TO plan should also account for non-contracted Black Start Unit capabilities and incorporate these resources if possible.

f.	Building Stable Island(s)

  - The primary focus of TO plan should be on building stable islands with the ultimate goal of reaching synchronization points.  TO plans should also consider that while larger islands are more stable they might be more difficult to synchronize with neighboring islands.

g.	Reaching synchronization points

  - The TO plan should focus on restoring the system and not restoring service to customers.  The primary focus of the TO plan should be on building a stable island that reaches a designated synchronization point.

h.	Synchronizing islands

  - The TO plan should instruct operators to contact ERCOT when islands are ready to be synchronized.  Actual synchronization will occur with TOS communicating directly with each other.  ERCOT will coordinate frequency control.  For intra-company islands the plan should contain instructions for adding load and generation.

j.	Restoring load after synchronization

  - TO plans should note that after synchronization occurs between islands, ERCOT will direct the further addition of load and generation.  The TO will continue to add load, but it will be at the direction of ERCOT as specified in the Strategy section of this plan.

A COMMUNICATIONS section should address at least the following items:

    - ERCOT contact information

    - List of contracted Black Start Units

  - Plant and QSE contact information and location within system

c.	List of non-contracted Black Start Units native to Black Start Plan.

- Plant and QSE contact information an location within system

d.	List of additional generating plants native to Black Start Plan

- Plant and QSE contact information and location within system

- Startup characteristics of each plant.

e.	List and location of neighboring TOs

- Contact information and tie points within the system

An OPERATIONS section should address at least the following items.  A subsection for operations of each island also be included in the TO plan.

a.	Black Start Unit

- Unit startup and load pickup procedure

b.	Next start units

- Unit startup and load pickup procedure

c.	Loads

- Critical loads in each island

d.	Transmission paths

- Switching procedures for primary transmission corridor

- Switching procedure for secondary transmission corridor

- One line diagram of primary and secondary corridor from Black Start Unit to synchronization points

- Special considerations or procedures for switching lines belonging to another TO.

e.	Synchronization points

- Location and ownership of each synchronization point

- Synchronization procedures and special requirements for each location

ERCOT will review the plans and procedures for consistency and conformance with this guide and ensure that they are updated at least annually.  ERCOT will make annual reports during the first quarter to the Reliability and Operations Subcommittee of plan review and any testing activities of black start resources.  ERCOT shall verify that the number, size, and location of system Black Start Units are sufficient to meet system restoration plan expectations.  (NERC Planning Standards)