| OGRR Number | 121OGRR | OGRR Title | Fault Recording Equipment Maintenance and Testing |
| --- | --- | --- | --- |
| ###### Date |  | Oct. 11, 2002 |  |
| ## Submitter’s Information |  |  |  |
| Name |  | Mark Henry |  |
| E-mail Address |  | mhenry@ercot.com |  |
| Company |  | ERCOT Compliance |  |
| Company Address |  | 7620 Metro Center Drive, Austin, TX 78744 |  |
| Phone Number |  | 512-225-7021 |  |
| Fax Number |  | X7020 |  |

Comments

- Suggest slight rewording of proposed change in this bullet :

- Fault recording equipment must be operationally tested at least annually to ensure that the equipment is functional.  Acceptable tests are the production of a manually triggered record (remotely or at the device), or automatic record production due to a power system disturbance.

- Reason for strikeout of “Responsiveness to remote polling / interrogation of the equipment via a communications channel”.  This alone may not provide a valid test of the equipment’s primary functions for all types of devices.  These functions are the sampling of quantities and the storage/retrieval of event records from memory.  Polling, unless it is accompanied by utilitization of the device’s event storage memory, may be insufficient to validate the storage capability.  Remote interrogation, or communications, does not necessarily involve either the sampling of data or the storage.  It is acceptable for use remote interrogation and polling to trigger creation of new records instead of manual (ie on-site), but the records then need to be read from the device’s storage.