| OGRR Number | 111-OGRR |  | OGRR Title | EECP Steps 2 and 4 |
| --- | --- | --- | --- | --- |
| ###### Status |  |  | Posted |  |
| Operating Guide Section Requiring Revision |  |  | 4.5.3.2 |  |
| Protocol Section Requiring Revision, if any. |  |  | ## 5.6.6.1 [possibly] |  |
| Requested Resolution |  |  | ## __X__ Normal ____ Urgent |  |
| Revision Description |  |  | Update EECP Steps 2 and 4 to reflect current procedures and participants. |  |
| ###### Reason for Revision |  |  | EECP Step 2 includes EECP procedures meant for the transitional ERCOT pilot. TDSP’s names and load values need to be updated in EECP Step 4. |  |
| ## Sponsor |  |  |  |  |
| Name |  |  | Rick Keetch |  |
| E-mail Address |  |  | rkeetch@reliant.com |  |
| Company |  |  | Reliant Energy |  |
| Company Address |  |  | P. O. Box 4567, Houston, TX 77210 |  |
| Phone Number |  |  | 713-207-2526 |  |
| Fax Number |  |  |  |  |
| ## Timeline |  |  |  |  |
| Date Received |  | 10/05/2002 |  |  |
| Date Posted |  | 10/09/2002 |  |  |
| Comments Due |  | 10/30/2002 |  |  |
| ROS Review Date |  |  |  |  |
| TAC Consideration |  |  |  |  |

Proposed Operating Guide Language Revision

#### 4.5.3.2	EECP Steps

Step 1 – Maintain ERCOT Undeployed Responsive Reserve Service Resources To 2300 Mw

| OPERATOR | ACTION |
| --- | --- |
| ERCOT | - Start RMR units available in the time frame of the emergency. RMR units should be loaded to full capability. - Utilize available resources providing Replacement and Non-Spin Reserve Services that can be deployed to increase Responsive Reserves. - Utilize available DC tie capability that is not already being used by the market. - Notify the Southwest Power Pool Security Coordinator. - OOM uncommitted units available within the expected timeframe of the emergency. |
| QSE | - Notify ERCOT of any resources uncommitted but available in the timeframe of the emergency. |

Step 2 – Maintain ERCOT Undeployed Responsive Reserve Equal To Largest Unit In Operation Or Greater

| OPERATOR | ACTION |
| --- | --- |
|  | In addition to measures associated with STEP 1 |
| ERCOT | - Instruct TDSPs to reduce customer loads by using distribution voltage reduction measures, if deemed beneficial by the TDSP. - Instruct QSEs to deploy winning bidders of Responsive Reserve, which is supplied from Load acting as a Resource (controlled by high-set under-frequency relays), to remove such load. |
| ERCOT | - With approval of the affected Non-ERCOT control area, may instruct TDSPs to implement Block Load Transfer, which transfer load from the ERCOT control area to Non-ERCOT control areas. |

Step 3 Maintain System Frequency At 60 Hz

| OPERATOR | ACTION |
| --- | --- |
|  | In addition to measures under STEPS 1 & 2 |
| ERCOT | - Issue an appeal through public media for voluntary load reduction. - Confirm that all generators are at maximum generation and other Resources are being maximized. |

Step 4 Maintain System Frequency At 59.8 Hz Or Greater

| OPERATOR | ACTION |
| --- | --- |
|  | In addition to measures under STEPS 1 – 3. |
| ERCOT | Direct all TDSPs and their agents to shed firm load, in 100 MW blocks, distributed as agreed and documented in the ERCOT Operating procedures in order to maintain a steady state system frequency of 59.8 Hz. |
| TDSPs | Keep in mind the need to protect the safety and health of the community and the essential human needs of the citizens. |

Obligation for load shed is by DSP.  Load shedding obligations need to be represented by an entity with 7x24 operations and hotline communications with ERCOT and control over breakers.  [Use Transmission Operators (TOs) as list of entities.]

ERCOT Load Shed Table

| # Transmission Operator | Total Transmission Operator Load (MW) |
| --- | --- |
| Austin Energy | 3.97 |
| American Electric Power | 10.01 |
| Brazos Electric Power Cooperative | 3.15 |
| City Public Service of San Antonio | 6.90 |
| City of Bryan | 0.44 |
| City of College Station | 0.26 |
| City of Denton | 0.37 |
| City of Garland | 0.83 |
| Lower Colorado River Authority | 4.57 |
| Magic Valley Electric Cooperative | 0.20 |
| Oncor | 38.83 |
| Public Utility Board of Brownsville | 0.41 |
| Rayburn Country Electric Cooperative | 0.70 |
| CenterPoint Energy | 26.61 |
| South Texas Electric Coop-Medina Electric Coop | 0.60 |
| TEXLA | 0.14 |
| Texas New Mexico Power | 2.01 |
| ## ERCOT Total | 100.00 |

| ## Other TAC Subcommittee Review |  |
| --- | --- |
| PRS Review Date |  |
| PRS Protocols Impact Decision |  |
| WMS Review Date |  |
| RMS Review Date |  |
| ## TAC Action |  |
| TAC Vote Date |  |
| TAC Proposed Implementation Date |  |
| TAC Vote Results |  |