| OGRR Number | 111-OGRR | OGRR Title | EECP Steps 2 and 4 |
| --- | --- | --- | --- |
| ###### Recommended Action |  | Approve. |  |
| Recommended Effective Date |  | January 1, 2003 |  |
| OGRR Background |  | ## Update EECP Steps 2 and 4 to reflect current procedures and participants. EECP Step 2 includes EECP procedures meant for the transitional ERCOT pilot. TDSP’s names and load values need to be updated in EECP Step 4. |  |
| Reliability and Operations Subcommittee Recommendation |  | Approve as revised by the Operating Guides Revision Task Force. |  |

Recommended Language

#### 4.5.3.2	EECP Steps

Step 1 – Maintain ERCOT Undeployed Responsive Reserve Service Resources To 2300 Mw

| OPERATOR | ACTION |
| --- | --- |
| ERCOT | - Start RMR units available in the time frame of the emergency. RMR units should be loaded to full capability. - Utilize available resources providing Replacement and Non-Spin Reserve Services that can be deployed to increase Responsive Reserves. - Utilize available DC tie capability that is not already being used by the market. - Notify the Southwest Power Pool Security Coordinator. - OOM uncommitted units available within the expected timeframe of the emergency. |
| QSE | - Notify ERCOT of any resources uncommitted but available in the timeframe of the emergency. |

Step 2 – Maintain ERCOT Undeployed Responsive Reserve Equal To Largest Unit In Operation Or Greater

| OPERATOR | ACTION |
| --- | --- |
|  | In addition to measures associated with STEP 1 |
| ERCOT | - Instruct TDSPs to reduce customer loads by using distribution voltage reduction measures, if deemed beneficial by the TDSP. - Instruct QSEs to deploy winning bidders of Responsive Reserve, which is supplied from Load acting as a Resource (controlled by high-set under-frequency relays), to remove such load. |
| ERCOT | - With approval of the affected Non-ERCOT control area, may instruct TDSPs to implement Block Load Transfer, which transfer load from the ERCOT control area to Non-ERCOT control areas. |

Step 3 Maintain System Frequency At 60 Hz

| OPERATOR | ACTION |
| --- | --- |
|  | In addition to measures under STEPS 1 & 2 |
| ERCOT | - Issue an appeal through public media for voluntary load reduction. - Confirm that all generators are at maximum generation and other Resources are being maximized. |

Step 4 Maintain System Frequency At 59.8 Hz Or Greater

| OPERATOR | ACTION |
| --- | --- |
|  | In addition to measures under STEPS 1 – 3. |
| ERCOT | Direct all TDSPs and their agents to shed firm load, in 100 MW blocks, distributed as agreed and documented in the ERCOT Operating procedures in order to maintain a steady state system frequency of 59.8 Hz. |
| TDSPs | Keep in mind the need to protect the safety and health of the community and the essential human needs of the citizens. Whenever possible, TDSPs shall not manually drop load connected to under-frequency relays during the implementation of the Emergency Electric Curtailment Plan. |

Obligation for load shed is by DSP.  Load shedding obligations need to be represented by an entity with 7x24 operations and hotline communications with ERCOT and control over breakers.  [Use Transmission Operators (TOs) as list of entities.]

ERCOT Load Shed Table

| # Transmission Operator | Total Transmission Operator Load (MW) |
| --- | --- |
| Austin Energy | 3.97 |
| American Electric Power | 10.01 |
| Brazos Electric Power Cooperative | 3.15 |
| City Public Service of San Antonio | 6.90 |
| City of Bryan | 0.44 |
| City of College Station | 0.26 |
| City of Denton | 0.37 |
| City of Garland | 0.83 |
| Lower Colorado River Authority | 4.57 |
| Magic Valley Electric Cooperative | 0.20 |
| Oncor | 38.83 |
| Public Utility Board of Brownsville | 0.41 |
| Rayburn Country Electric Cooperative | 0.70 |
| CenterPoint Energy | 26.61 |
| South Texas Electric Coop-Medina Electric Coop | 0.60 |
| TEXLA | 0.14 |
| Texas New Mexico Power | 2.01 |
| ## ERCOT Total | 100.00 |

| ## Other TAC Subcommittee Review |  |
| --- | --- |
| PRS Review Date | 26 November 2002 |
| PRS Protocols Impact Decision | No impact on the Protocols. |
| WMS Review Date |  |
| RMS Review Date |  |
| ## TAC Action |  |
| TAC Vote Date |  |
| TAC Proposed Implementation Date |  |
| TAC Vote Results |  |

| OGRR Evaluation |  |
| --- | --- |
| Comments Author | Comments Summary |