| OGRR Number | 121OGRR | OGRR Title | Fault Recording Equipment Maintenance and Testing |
| --- | --- | --- | --- |
| ###### Recommended Action |  | Approve |  |
| Recommended Effective Date |  | January 1, 2003 |  |
| OGRR Background |  | ## Modify wording that allows manual and automatic triggers to count as a functional test as well as recorder event waveform analysis and verifications to count as calibration checks. This language was approved at the July 2001 SPWG meeting and proposed to ROS in August 2001. Revision to Appendix B, B.2.2.5 |  |
| Reliability and Operations Subcommittee Recommendation |  | ROS recommends approval as revised. |  |

Recommended Language

#### B.2.2.5	Maintenance and Testing Requirements

Facility Owners shall maintain and test their Fault recording equipment as follows:

- In accordance with the manufacturer’s recommendations.

- Calibration of the analog (waveform) channels shall be performed at installation and when records from the equipment indicate a calibration problem.  Calibration can be monitored through the analysis and correlation of fault records with system models and the records of other fault recorders in the area.

- Fault recording equipment must be operationally tested at least annually to ensure that the equipment is functional.  Acceptable tests are the production of a manually triggered record (remotely or at the device), or automatic record production due to a power system disturbance.

| ## Other TAC Subcommittee Review |  |
| --- | --- |
| PRS Review Date | 26 November 2002 |
| PRS Protocols Impact Decision | No impact on the Protocols. |
| WMS Review Date |  |
| RMS Review Date |  |
| ## TAC Action |  |
| TAC Vote Date |  |
| TAC Proposed Implementation Date |  |
| TAC Vote Results |  |

| OGRR Evaluation |  |
| --- | --- |
| Comments Author | Comments Summary |
| OGRTF | Revised language. |