| PRR Number | 218PRR | PRR Title | Responsibility Assignment for Reactive Power Capability & AVR |
| --- | --- | --- | --- |
| ###### Status |  | Approved by Board as modified by PRS on 5/10/2001. |  |
| Protocol Section Requiring Revision |  | 6.10.3.5, Reactive Supply from Generation Resources |  |
| Requested Resolution |  | ## Normal |  |
| Revision Description |  | Change the responsibility for reactive power capability verification and automatic voltage regulator (AVR) testing from the QSE to the Generation Entity. |  |
| ###### Reason for Revision |  | Generators can change their QSE at will. There is no way to hold QSEs accountable for these requirements that are directly associated with operating power plants. |  |
| ## Timeline |  |  |  |
| Date Received |  | 4/11/2001 |  |
| Date Posted |  | 4/16/2001 |  |
| Comments Due |  | 5/07/2001 |  |
| PRS Review Date |  | 5/10/2001 |  |
| PRS Recommendation |  | Approve as modified. |  |
| TAC Consideration |  | 6/06/01 – Approved |  |
| Board Consideration |  | 6/19/01 - Approved |  |

Proposed Protocol Language Revision

#### 6.10.3.5   Reactive Supply from Generation Resources

- The Generation Entity must verify and maintain its stated Reactive Power capacity for each of its Generation Resources, as required by the NERC Planning Standards “System Modeling Data Requirements, Generation Equipment.” Sections 2.B, Measurement 3 and as may be required by the Operating Guides. Generation Resources reactive capability limits shall be specified considering nominal substation voltage.

- The QSE will conduct reactive capacity qualification tests to verify the maximum leading and lagging reactive capacity of all Generation Resources, which it represents.  Reactive capacity tests will be performed on initial qualification and periodically at an ERCOT-set interval no more often than once every two years, unless ERCOT has information indicating that current data is inaccurate. The QSE is not obligated to place Generation Resources on line solely for testing.

- Maximum lagging power factor reactive operating limit shall be demonstrated during peak Load season, at the net dependable megawatt capability, insofar as system voltage conditions and other factors will allow. The Generation Resource should be required to maintain this level of reactive power for at least fifteen (15) minutes.

- Maximum leading power factor reactive operating limit shall be demonstrated during light Load conditions, with the unit operating at its minimum Load, insofar as system voltage conditions and other factors will allow. The unit should be required to maintain this level of reactive power for at least fifteen (15) minutes.

- The Generation Entity shall perform the unit automatic voltage regulator (AVR) tests and shall supply AVR data as required by the NERC Planning Standards “System Modeling Data Requirements, Generation Equipment.” Sections 2B, Measurement 4, and 2B, Measurement 6 and as may be specified in the Operating Guides. The AVR tests will be performed on initial qualification and periodically at an ERCOT-set interval no more often than once every five years. The AVR tests are run at a time agreed on in advance by the QSE, TDSP, and ERCOT.

| ## Sponsor |  |
| --- | --- |
| Name | Beth Garza |
| E-mail Address | Beth_garza@fpl.com |
| Company | FPL Energy |
| Company Address | 701 Brazos, Suite 500, Austin 78746 |
| Phone Number | 512-320-9171 |
| Fax Number | 512-320-5821 |
| ## ERCOT Impact Analysis |  |
| Date |  |
| Financial Impact |  |
| Analysis |  |
| ## TAC Action |  |
| TAC Vote Date | 6/06/2001 |
| TAC Proposed Implementation Date | July 1, 2001 |
| TAC Vote Results | Approved |
| ## ERCOT Board Action |  |
| ERCOT Board Vote Date | 6/19/2001 |
| ERCOT Board Implementation Date | July 1, 2001 |
| ERCOT Board Results | Approved |
| ## Appeal |  |
| Appeal Date |  |
| Entity Initiating Appeal |  |
| Nature of Appeal |  |