| PRR Number | 219PRR | PRR Title | Frequency Level Deviation |
| --- | --- | --- | --- |
| ###### Status |  | Approved by Board. |  |
| Protocol Section Requiring Revision |  | 6.10.5.4 Responsive Reserve Services Monitoring Criteria |  |
| Requested Resolution |  | ## Normal |  |
| Revision Description |  | Change the level of frequency deviation at which ERCOT measures and records various system operating data from 0.375 to 0.175 Hz |  |
| ###### Reason for Revision |  | Current practice is to collect data from the existing Control Areas for deviations of 0.175Hz. There is no reason to change that practice under single control area operation. |  |
| ## Timeline |  |  |  |
| Date Received |  | 4/11/2001 |  |
| Date Posted |  | 4/16/2001 |  |
| Comments Due |  | 05/07/2001 |  |
| PRS Review Date |  | 05/10/2001 |  |
| PRS Recommendation |  | Approve as submitted. |  |
| TAC Consideration |  | 6/06/2001 – Approved. |  |
| Board Consideration |  | 6/19/2001 – Approved. |  |

Proposed Protocol Language Revision

#### 6.10.5.4	Responsive Reserve Services Monitoring Criteria

QSEs providing Responsive Reserve Services must so indicate in the Scheduling process. On deployment of any Responsive Reserve service, the QSE shall control its Resources to operate to the final Resource bilateral schedules as converted to a base power function plus the Instructed Responsive Reserve power requirement. ERCOT calculation of SCE 10 minutes after the deployment instruction will determine the level of Responsive Reserve Service provided. Satisfactory control performance of the QSE providing only Responsive Reserve Services shall be deemed satisfactory when:

- Not less than 95% nor more than 120% of the RRS requested, subject to the declared capabilities of the QSE, is provided within ten (10) minutes of ERCOT’s deployment Dispatch Instruction and maintained until recalled or expiration of the QSEs service obligation, and

- The RRS requested shall return to within 90% to 110% of its pre-deployment scheduled output, subject to the declared capabilities of the QSE, within ten (10) minutes following a recall instruction from ERCOT.

For all frequency deviations exceeding 0.3750.175 Hz, ERCOT shall measure and record each two (2) second scan rate values of real power output for each QSE Resource providing Responsive Reserve. ERCOT shall measure and record the MW data beginning one (1) minute prior to the start of the frequency excursion event until ten (10) minutes after the start of the frequency excursion event. Satisfactory performance is measured by comparing the actual response to the frequency response capability response required in the Operating Guides.

Where multiple observations of operating response are available, the QSE must deliver the required frequency response capability 75% of the time during any single calendar quarter.

| ## Sponsor |  |
| --- | --- |
| Name | Beth Garza |
| E-mail Address | beth_garza@fpl.com |
| Company | FPL Energy |
| Company Address | 701 Brazos, Suite 500, Austin 78701 |
| Phone Number | 512-320-9171 |
| Fax Number | 512-320-5821 |
| ## ERCOT Impact Analysis |  |
| Date |  |
| Financial Impact |  |
| Analysis |  |
| ## TAC Action |  |
| TAC Vote Date | 6/06/2001 |
| TAC Proposed Implementation Date | July 1, 2001 |
| TAC Vote Results | Approve |
| ## ERCOT Board Action |  |
| ERCOT Board Vote Date | 6/19/2001 |
| ERCOT Board Implementation Date | July 1, 2001 |
| ERCOT Board Results | Approve |
| ## Appeal |  |
| Appeal Date |  |
| Entity Initiating Appeal |  |
| Nature of Appeal |  |