| PRR Number | 267PRR | PRR Title | Black Start Basic Startup Test Interval |
| --- | --- | --- | --- |
| ###### Status |  |  |  |
| Protocol Section Requiring Revision |  | 6.10.3.6 |  |
| Requested Resolution |  | ## Normal |  |
| Revision Description |  | Clarify requirements for annual testing of black start units. |  |
| ###### Reason for Revision |  | Protocols 6 is not clear on whether one or three year test interval is required for blackstart units. One year testing (basic start test) seems to be the overriding intent of the Protocols. Furthermore, one year testing is necessary to meet NERC Planning Standards. The 3 year testing and 6 year testing described include the basic start test. So in years that those tests are performed, the basic start test will also be done in the process. |  |
| ## Timeline |  |  |  |
| Date Received |  | 7/24/2001 |  |
| Date Posted |  | 7/26/2001 |  |
| Comments Due |  | 8/16/2001 |  |
| PRS Review Date |  | 8/--/2001 |  |
| PRS Recommendation |  |  |  |
| TAC Consideration |  |  |  |
| Board Consideration |  |  |  |

Proposed Protocol Language Revision

#### 6.10.3.6 System Black Start Capability

- Qualification will be provided to any Black Start Resource that has met the following requirements:

  - Verified control communication path performance;

  - Verified primary and alternate voice circuits for receipt of instructions;

  - Passed the basic starting test;

  - Passed the line energizing test; and

  - Passed the Load carrying test.

- On successful demonstration of system Black Start Service capability, ERCOT shall qualify the Black Start Resource as being permitted to provide the system Black Start Service capacity and shall provide a copy of the certificate to the Black Start Resource. Qualification shall be valid for one year from the date of the last successful Basic Starting test, three years from the date of the last successful line energizing test, or six years from the date of the last successful Load carrying test, whichever is earliest. Qualification shall be revoked if the Black Start Resource fails to perform successfully during an actual restoration event, until the Black Start Resource is successfully retested. Retesting is only required for the aspect of system Black Start Service capability (basic starting, line energizing, or Load carrying) for which the Black Start Resource failed.

  - Basic Starting Test

    - The basic ability of the Black Start Resource to start itself, without support from the ERCOT System, is tested annually , either as a stand-alone test or part of the line energizing and load carrying tests. The test is run during a one-week period agreed on in advance by the Black Start Resource and ERCOT.

    - ERCOT shall confirm the dates of the test with the Black Start Resource;

    - At a time during a previously agreed test week window not previously disclosed to the Black Start Resource, ERCOT will initiate the test;

    - The Black Start Resource, including all auxiliary Loads, will be isolated from the power system;

    - The Black Start Resource will start without assistance from the system; and

    - The Black Start Resource must remain stable (in both frequency and voltage) while supplying only its own auxiliary Loads or Loads in the immediate area for at least 30 minutes.

| ## Sponsor |  |
| --- | --- |
| Name | Robert Potts |
| E-mail Address | rpotts@lcra.org |
| Company | LCRA |
| Company Address | LCRA P O Box 220 Austin TX 78767 |
| Phone Number | 512-482-6279 |
| Fax Number | 512 385-2146 |
| ## ERCOT Impact Analysis |  |
| Date |  |
| Financial Impact |  |
| Analysis |  |
| ## TAC Action |  |
| TAC Vote Date |  |
| TAC Proposed Implementation Date |  |
| TAC Vote Results |  |
| ## ERCOT Board Action |  |
| ERCOT Board Vote Date |  |
| ERCOT Board Implementation Date |  |
| ERCOT Board Results |  |
| ## Appeal |  |
| Appeal Date |  |
| Entity Initiating Appeal |  |
| Nature of Appeal |  |