Observations concerning Droop Settings

ROS December 10, 2002 meeting

- Runs compared:

  - Series 3: 700 MW drop with UFLS, 5% Droop

  - Series 31: 700 MW drop with UFLS, 7% Droop

  - Series 32: 700 MW drop with UFLS, 9% Droop

  - Series 1: 2500 MW drop with UFLS, 5% Droop

  - Series 33: 2500 MW drop with UFLS, 7% Droop

  - Series 34: 2500 MW drop with UFLS, 9% Droop

- For the 700 MW drop runs, the major problem encountered is over-frequency.

  - For the 5% droop runs  (Series 3) 25 combinations fail.

  - For the 7% droop runs  (Series 31) 59 combinations fail.

  - For the 9% droop runs  (Series 32) 59 combinations fail.

- For the 2500 MW drop runs, the major problem encountered is under-frequency.

  - All runs were acceptable with 75%, or 50% interruptible load

  - For the 5% droop runs, with 25% interruptible load (Series 1): No combinations fail: frequency decays to 59.27 Hz, and recovers to 59.76 Hz.

  - For the 7% droop runs, with 25% interruptible load (Series 33): All combinations fail: frequency decays to 59.02 Hz, and doesn’t recover.

  - For the 9% droop runs, with 25% interruptible load (Series 34): All  combinations fail: frequency decays to 58.90 Hz, and doesn’t recover.  We would probably get some amount of UFLS Stage 2 tripping.

  - For the 5% droop runs, with no interruptible load (Series 1): frequency decays to 59.27 Hz, and recovers to 59.7 Hz.

  - For the 7% droop runs, with no interruptible load (Series 33): frequency decays to 58.88 Hz, and doesn’t recover.  UFLS Stage 2 would trip.

  - For the 9% droop runs, with no interruptible load (Series 34): frequency decays to 58.88 Hz, and doesn’t recover.  UFLS Stage 2 would trip.

Effect on Summary Tables:

Limit of interruptible load that can be used to replace Responsive Reserve

Based on Main Scenarios – Spring Off-Peak case

Original Responsive Reserve study – 5% Droop:

|  | Case 1 - 25% 575 MW | Case 2 -50% 1150 MW | Case 3 -75% 1725 MW | Case 4 -100% 2300 MW |
| --- | --- | --- | --- | --- |
| Level a: 59.7 | Any | Any | <= 60 % | N/A |
| Level b: 59.8 | Any | Any | <= 45 % | N/A |
| Level c: 59.9 | Any | Any | <= 60 % | N/A |

Base Case – 0 MW interruptible – 2300 MW from generation – OK

Limit of interruptible load that can be used to replace Responsive Reserve

Based on Main Scenarios – Spring Off-Peak case

Using 7% or 9% Droop settings:

|  | Case 1 – 25% 575 MW | Case 2 -50% 1150 MW | Case 3 -75% 1725 MW | Case 4 -100% 2300 MW |
| --- | --- | --- | --- | --- |
| Level a: 59.7 | All FAIL | Any | <= 50 % | N/A |
| Level b: 59.8 | All FAIL | Any | <= 30 % | N/A |
| Level c: 59.9 | All FAIL | Any | <= 50 % | N/A |

Base Case – 0 MW interruptible – 2300 MW from generation – FAILS

Vance Beauregard, AEP

2002 DWG Chairman