# PDCWG Report

# December 04, 2002

Attendees:

John Dumas		TXU

Sydney Niemeyer	Reliant Energy

George Niels		Austin Energy

Jeff Healy		ERCOT

Wayne Kemper	Reliant Energy

Phillip Blevins		STEC

Henry Zamora		Austin Energy

Paul Dougherty	Calpine

Joe Cherri		Garland

The group continued the discussion of an ERCOT Frequency Response Standard.  The QSE reports use a standard of (420 MW/. 1 Hz) as the basis of measurement for QSE performance.  This standard was chosen by the PDCWG as a good conservative number of generation resource response based on historical data collected in 2000.  The PDCWG believes that if the ERCOT grid continues to receive a resource response of 420 MW/.1 Hz or greater, ERCOT will remain stable.

There is a concern that under the current 20% responsive reserve rule that a QSE representing a single generator could get an allocation of the 420 M/.1Hz that would exceed a 5% droop measure.  Example a 750 MW unit could supply 150 MW of responsive reserve service.  The frequency response share would be 150 MW/(2300 MW *  75%)*420 MW = 36.5 MW/.1Hz which would exceed a 5% droop measure of 750 MW/30 = 25 MW /.1Hz.  Because of this scenario the PDCWG is recommending that a QSE’s frequency response share would be the lesser of a 5% droop or the frequency response share of the 420 MW/.1Hz.

Handouts of the current report format will be passed out at the ROS meeting and the calculation will be presented