ERCOT Operations Report

@

ROS & OWG

For November 2002

Frequency control issues (High or Low Frequency) 59.9 > F > 60.1.

| Time | Frequency | Event |
| --- | --- | --- |
| 11/1/2002 6:14 | 59.89599991 |  |
| 11/1/2002 6:19 | 59.89500046 |  |
| 11/1/2002 11:03 | 60.10599899 | Loss of a QSE's internal load caused large positive SCE |
| 11/1/2002 17:02 | 60.14500046 | Insufficient regulation to cover schedule change. |
| 11/1/2002 22:02 | 59.86399841 | At 2200 a QSE's base power schedule dropped from 975 to 0 |
| 11/1/2002 22:16 | 60.10400009 |  |
| 11/4/2002 9:46 | 59.87400055 | Unit dropped from 800 to 350 due to loss of feed pump. |
| 11/5/2002 0:12 | 60.10100174 | QSE reported units not responding to AGC and have switched to manual to correct. |
| 11/5/2002 8:59 | 59.85699844 | 618 MW unit trip. |
| 11/5/2002 12:04 | 59.83000183 | 540 MW unit trip. |
| 11/5/2002 22:10 | 60.11500168 |  |
| 11/6/2002 6:00 | 59.89899826 |  |
| 11/7/2002 21:53 | 59.89400101 | 700 MW unit trip. |
| 11/11/2002 22:10 | 60.13700104 |  |
| 11/13/2002 22:04 | 59.89899826 |  |
| 11/14/2002 8:35 | 60.10800171 |  |
| 11/15/2002 10:17 | 59.83399963 | 570 MW unit trip. |
| 11/16/2002 20:02 | 59.86100006 | Unit dropped from 800 to 200 during an error while testing. |
| 11/16/2002 20:41 | 59.72200012 | Unit tripped carrying ~ 1250 MW. 560 MW of UF load shed activated. |
| 11/18/2002 19:51 | 59.86399841 | 580 MW unit trip. |
| 11/19/2002 6:03 | 59.89199829 | Unit trip. |
| 11/19/2002 6:11 | 59.88899994 |  |
| 11/20/2002 13:52 | 59.8769989 | 400 MW unit trip. |
| 11/22/2002 6:11 | 59.84999847 | Multiple QSE's with large SCE |
| 11/23/2002 22:11 | 60.11100006 |  |
| 11/24/2002 7:52 | 59.83599854 | 600 MW unit trip. |
| 11/26/2002 22:03 | 59.88399887 | DC tie tripped. |
| 11/27/2002 6:11 | 59.89599991 | Station tripped; 412 MW total generation lost. |
| 11/29/2002 18:05 | 60.11600113 | Multiple QSE's with large SCE |

(Frequency deviations with no event noted are occurring during periods of largest schedule change)

## Congestion Management Occurrences & Related Problems

*Days of units purchased for some time in the area described.  Data taken form daily reports and is approximate.  For global overview purposes only.

Major Computer Systems Problems/ Fixes.

None Applicable

New Procedures/ Forms/ Operations Bulletins.

The following details of new Operations Bulletins were posted on the dates described:

11/4

- ERCOT has completely rewritten the Operating Procedures Development and Maintenance section of the Operating Procedure Manual.  This document describes the process ERCOT staff follows in revising its Power System operating procedures.

- Implement new RMR resource scheduling procedures in the Day Ahead Desk Operating Procedure Manual.  (Sections 2.1.5& 2.1.13 & attachments.)  (TCN #1).

- Revised the Operating Period Desk procedure to clarify steps the ERCOT operator is to take when a QSE’s resources are incapable of providing the scheduled Responsive Reserve Service.  (TCN #2)

- Implementation of relaxed Balanced Scheduling for the Frequency Desk.  (TCN #4)

- Implementation of State Estimator, Transmission & Security Desk, Appendix 3.  (TCN #5)

11/14

- Implementation of ERCOT Direct Current Ties.

- Implementation of ERCOT System Operator Logging Guideline.

- Revised the Outage Coordinator section of the Operating Procedure Manual to address units who cannot respond within 2 hours.

11/19

- Revised the Day Ahead section of the Operating Procedure Manual.  Most changes were made to incorporate TCNs added since the last revision in April 2002.  Some changes were made to improve the readability of certain procedure steps without changing the activity.

- Revised the Transmission and Security section of the Operating Procedure Manual.  Most changes were made to incorporate TCNs added since the last revision in April 2002.  Some changes were made to improve the readability of certain procedure steps without changing the activity.

Security Alert Stage/ Threatcon/ Related issues.

Threatcon LOW throughout November.

Describe each EECP Occurrence.

None

OCN, Alert, Energy Notice and Major Disturbances

11/10	OCN issued due to loading on Rio Hondo  - La Palma 345 kV.

11/28	OCN issued due to loading on North – to – Temple 345 kV

Major Weather Related Power System Problems

none

Significant Communication Problems

Communications Advisories were sent out for the following issues:

11/8	Loss of MOI communications for the 06:30 interval.

11/10	Loss of Portal.

11/13	Loss of Portal.

11/14	Loss of Portal.

11/20	Could not communicate Market Deployments.

11/22	Loss of Portal.

11/26	Loss of Portal.

11/27	Loss of Portal.

Major system Voltage problems

None

Blackout/Load Shed incidences

11/16/02   20:42	UF LAARS operated when frequency went below 59.70mw. QSE ‘A’ shed about 400mw on under frequency and QSE ‘B’ dropped about 160mw of load on under frequency.

ERCOT peak for last month (Unofficial)

11/26/2002 19:45    35904

# Update on new generation

No new generation commercially available in November.

New SPS & RAP’s

None

Issues with ERCOT entities

None