ERCOT Operations Report

@

ROS & OWG

For December 2002

Frequency control issues (High or Low Frequency) 59.9 > F > 60.1.

| Time | Frequency |  | Event | SCE | Reg. Deployed (Trend) |
| --- | --- | --- | --- | --- | --- |
| 12/3/2002 5:58 | 60.106 |  |  | 255 | 22.6 (Decreasing) |
| 12/3/2002 6:09 | 59.890 |  |  | 140 | -479.2 (Increasing) |
| 12/9/2002 10:09 | 59.880 |  |  | -210.6 | 260.4 (Increasing) |
| 12/14/2002 22:06 | 59.814 |  | MLSES 1 tripped, 732 MW | N/A | N/A |
| 12/15/2002 18:09 | 59.689 |  | STP 2 tripped, 1250 MW | N/A | N/A |
| 12/16/2002 5:58 | 59.885 |  |  | -240.1 | -504.2 (Increasing) |
| 12/16/2002 22:05 | 60.106 |  |  | -139.7 | 577.56 (Decreasing) |
| 12/17/2002 22:04 | 59.894 |  |  | -1302.1 | 187 (Increasing) |
| 12/17/2002 22:14 | 60.101 |  |  | -152.8 | -150.2 (Decreasing) |
| 12/18/2002 22:09 | 59.886 |  | Spruce 1 tripped, 600 MW | N/A | N/A |
| 12/18/2002 23:06 | 60.107 |  |  | 526 | 225 (Decreasing) |
| 12/19/2002 5:56 | 60.101 |  |  | 1271.9 | -1708.6 (Decreasing) |
| 12/19/2002 6:24 | 59.837 |  |  | -633.2 | -514.6 (Increasing) |
| 12/20/2002 5:14 | 59.894 |  |  | -806.4 | 668.4 (Increasing) |
| 12/20/2002 16:25 | 59.870 |  | MNSES 3 tripped, 660 MW | N/A | N/A |
| 12/23/2002 22:09 | 59.867 |  |  | -80.7 | 122.7 (Increasing) |
| 12/24/2002 5:53 | 60.108 |  |  | 1074.1 | -1144.5 (Increasing) |
| 12/27/2002 22:51 | 59.836 |  | CBY 2 tripped, 550 MW | N/A | N/A |

(Frequency deviations with no event noted are occurring during periods of largest schedule change)

## Locations and Relative Activity of Congestion Management

*Days of units purchased for some time in the area described.  Data taken form daily reports and is approximate.  For global overview purposes only.

Major Computer Systems Problems/ Fixes.

None Applicable

New Procedures/ Forms/ Operations Bulletins.

ERCOT Market Operations Bulletin # 9 was posted on:

12/16

- Recovery of additional costs for OOME down for wind resources.

Security Alert Stage/ Threatcon/ Related issues.

Threatcon LOW throughout December.

Describe each EECP Occurrence.

None.

OCN, Advisory, Alert, Energy Notice and Major Disturbances

12/04	18:37	OCN issued due to loading in DFW area.

12/04	19:00	OCN issued due to cold weather in North/Central ERCOT region.

12/20	09:00	Advisory issued due to site to site failover.

Major Weather Related Power System Problems

None.

Significant Communication Problems

Communications Advisories were sent out for the following issues:

12/08	Could not communicate Market Deployments.

12/15	Loss of Portal.

12/18	Could not communicate Market Deployments.

12/20	Loss of Portal.

12/26	Loss of Portal.

12/31	Loss of Portal.

Major system Voltage problems

None

Blackout/Load Shed incidences

12/15/2002  18:09  STP #2 tripped with 1250 MW. Frequency spiked to 59.689 and recovered in 11 min. at 1820. UFR's did trip approximately 450 MW of load. At 18:30 a Hotline call was made notifying QSE'e to reinstate their UFR's.

ERCOT peak for last month (Unofficial)

12/06/2002 07:15  	39710

# Update on new generation

No new generation commercially available in December.

Max / Min Temperature

12/3/2002	Abilene		28 F

12/5/2002 	Browsnville	81 F

New SPS & RAP’s

None

Others

12/18/02  19:29	ERCOT opened a second A/S market from 20:00 to 22:45.

12/31/02	  22:45	ERCOT held interval 23:45 for 00:00 & 00:15.