| PRR Number | 380PRR | PRR Title | Various Black Start Service Changes |
| --- | --- | --- | --- |
| ###### Date |  | 1-21-2003 |  |
| ## Submitter’s Information |  |  |  |
| Name |  | Jack Thormahlen |  |
| E-mail Address |  | Jack.thormahlen@lcra.org |  |
| Company |  | LCRA |  |
| Company Address |  | P.O. Box 220, Austin, Texas 78767-0220 |  |
| Phone Number |  | 512-4730-3200 ext. 2635 |  |
| Fax Number |  | 512-469-6856 |  |

Comments

Base on negotiations with Manuel Munoz of CenterPoint and the ERCOT compliance staff via Robert Potts, the following is offered:

#### 6.10.3.6	System Black Start Capability

- Qualification will be provided to any Black Start Resource that has met the following requirements:

  - Verified control communication path performance;

  - Verified primary and alternate voice circuits for receipt of instructions;

  - Passed the basic starting test;

  - Passed the line energizing test; and

  - Passed the Load carrying test.

- On successful demonstration of system Black Start Service capability, ERCOT shall qualify the Black Start Resource as being permitted to provide the system Black Start Service capacity and shall provide a copy of the certificate to the Black Start Resource. Qualification shall be valid for one year from the date of the last successful Basic Starting test, three years from the date of the last successful line energizing test, or six years from the date of the last successful Load carrying test, whichever is earliest. Retesting is only required for the aspect of system Black Start Service capability (basic starting, line energizing, or Load carrying) for which the Black Start Resource failed.

The deletion of the sentence in 6.10.3.6(2) is due to the section in all other respects addresses testing and retesting. The revoking of qualification is inappropriate in this section and has been addressed in Section 6.10.3.6(3).

An additional item to be addressed in the Standard Form Black Start Agreement is the definition of “Available” in Section 9B(1). The following is offered:

Section 9.Payment

B.	Hourly Standby Fee Payments. ERCOT shall pay Participant the Hourly Standby Fee, except as specified otherwise in Section 7 above.

- (1)	“Available” means, with respect to a given hour, that Participant has declared, in its Availability Plan, that the Black Start Resource is able to black start without a connection to the ERCOT Transmission Grid. The Black Start Resource will not be considered “Available” from the time the Black Start Resource fails the Black Start Test to the time the Black Start Resource passes the Black Start Test, as defined in the Operating Guides, or has failed to black start when required to black start under this Agreement, and the Black Start Resource has not since passed a subsequent Black Start Test.