Meter Working Group Meeting Agenda

January 30, 2003

Meeting Location – ERCOT Taylor Control Center

Meeting Time – 9:30 – 3:30

- Annual Elections of Chair and Vice Chair for the MWG

(9:30 – 10:00)

Current nominations that have obtained their companies approval and agreed to serve a term as chair and/or vice chair of the MWG are listed below:

Elections were held by ballot and the results are below:

Chair:

# Dwane Tervooren of AEP-WTU TDSP

Vice Chair:

Dale Tinnin of Centerpoint TDSP

- Further Discussion of the Meter Working Group Procedures Document (10:00 – 10:45)

A draft was commented on during the meeting and will be distributed to the group for review.  A final draft will be presented at the next MWG meeting for review and conclusions.

Need to determine the reporting requirements to fulfill the needs of WMS.

Was resolved with language in the MWG procedures draft document.

- Discussion on Ratio Checking Optical Current Transformers for the five year certification / testing requirements in Protocols

(10:45 – 12:00)

Mark Rollins will check with Alstrom about their testing procedure and provide a copy of it for review next month.

Ken Swift will coordinate a conference call with Dale Tinnin, ERCOT, and ABB to discuss their MOCT testing procedure.

All interested parties wanting to participate should notify Ken Swift.

- Update on status of meter alarm programming  –

(12:45 – 1:45)

Notes from the September 18, 2002 meeting minutes:

- TDSP’s will report on what alarms are being programmed into the EPS meters.

- ERCOT will perform research to determine the code that MV90 looks for, by meter type, to flag the events listed in section 5.4 of SMOG.

- After this information is obtained, a sub team will determine if a standard treatment for logging the events can be accomplished.  This will be meter specific.

  - Oncor will look at the ION meter

  - Centerpoint will look at the Trans Data meter

  - Austin Energy will look at the Schlumberger and Jem Star meters

  - TNMP will look at the Siemens meter

Patrick Vinton reported for ERCOT about the research he did with ITRON and the other meter vendors addressing the event coding and alarms.  Patrick presented a spreadsheet that demonstrated what alarms each metering vendor currently supplied to MV90 and the code that MV90 assigned to it.  A crosscheck spreadsheet was also presented that demonstrated which of the protocols required event/alarms are not identified by MV90 with a usable code for each meter.

  - Oncor will work with Power Measurement ION to get them to contact ITRON and report back to the group at the next MWG meeting.

  - Centerpoint will work with Transdata to get them to contact ITRON and report back to the group at the next MWG meeting.

  - Austin Energy will work with Schlumberger to get them to contact ITRON and report back to the group at the next MWG meeting.

  - TNMP will work with Siemens to get them to contact ITRON and report back to the group at the next MWG meeting.

MWG decide to table for a future meeting the discussions around what the possible benefits and impacts may be around expanding alarm/event reporting.

- Update and discussion of a cutover process for new EPS metering Facilities or making changes to the netting scheme for existing EPS Facilities.

(1:45 – 2:30)

ERCOT will send copies of the redlined and clean copies of the cutover form to the MWG distribution list.

TDSP’s agreed to use it on a trial basis until the next MWG meeting.

- Discussion and comments on the EPS Site Audit Checklist.

(2:30 – 3:15)

Notes from the September 18, 2002 meeting minutes:

- Document needs formatting

- TDSP’s will utilize this checklist during an upcoming site certification and provide feedback on the checklist.

The EPS Site Audit Checklist discussion was deferred to the next meeting.

- Date of next meeting:  TBD

(3:15 – 3:30)

- Discussion about CCVT accuracy testing.

TDSPs were encouraged to maintain detailed documentation about their testing of CCVTs.  Items mentioned were:

- As found/ as left testing

- Manufacturers nameplate data

- Date of manufacture

This documentation would be used at a later date to make a determination about the disposition of CCVTs long term in EPS Metering installations.

A discussion about utilizing comparative data to confirm CCVT accuracy performance resulted in the conclusion that after performance had been successfully proven over time this data might be utilized in lieu of other testing reports.  A Protocols change will be required with this option.

Additional topics discussed:

ERCOT was requested to send a notice to the MWG distribution list about the Competitive Metering kickoff meeting.