| PRR Number | 380PRR | PRR Title | Various Blackstart Changes |
| --- | --- | --- | --- |
| ###### Date |  | 2/3/03 |  |
| ## Submitter’s Information |  |  |  |
| Name |  | Dennis Kunkel |  |
| E-mail Address |  | dkkunkel@AEP.com |  |
| Company |  | AEP Service Corp, Corpus Christ Texas 78405 |  |
| Company Address |  | 5502 Corporate Dr |  |
| Phone Number |  | 3612894003 |  |
| Fax Number |  | 3612894030 |  |

Comments

AEP TDSP suggested that the underlined language in the following sections be added in order to allow contracted capacity from power pools that are ac isolated from ERCOT in the bid evaluation and that we also clearly require that any selected blackstart service be studied to determine if it can start the next start unit before selecting it.

### Black Start Service

As provided by a Generator, contracted power supply from other power pools that are always ac isolated from ERCOT, or a QSE to ERCOT: The provision of power supply Resources under a Black Start Agreement, pursuant to emergency dispatch, which are capable of self-starting or starting from another power pool via a power supply contract without support from the ERCOT System in the event of a blackout.

#### 6.10.3.6	System Black Start Capability

- Qualification will be provided to any Black Start Resource that has met the following requirements:

  - Verified control communication path performance;

  - Verified primary and alternate voice circuits for receipt of instructions;

  - Passed the basic starting test;

  - Passed the line energizing test; and

  - Passed the Load carrying test.

  - Passed simulation studies that show that the resource can start the next start unit’s largest required motor while meeting the next start units minimum startup load requirements