ERCOT Operations Report

ROS & OWG

For January 2003

Frequency control issues (High or Low Frequency) 59.9 > F > 60.1

| Time | Frequency | Event | SCE | Reg. Deployed (Trend) | Load |
| --- | --- | --- | --- | --- | --- |
| 1/8/03 22:02 | 59.808 | QSE was getting a down regulation instruction during the 22:00 ramp because their pre-ramp SCE was +460. The QSE's SCE dropped to -1100 during the ramp. Approximately 160 MW interruptible load tripped. | -1385 | 365 (Increasing) | Decreasing |
| 1/10/03 6:13 | 59.886 |  | -805 | -135 (Increasing) | Increasing |
| 1/12/03 7:51 | 60.101 | 08:00 and 08:15 interval held due to bad STLF. VDI issued. | 427 | -325 (Decreasing) | No Trend |
| 1/13/03 22:09 | 60.123 |  | 82 | -1255 (Decreasing) | No Trend |
| 1/15/03 18:03 | 60.104 |  | 295 | -815 (Decreasing) | No Trend |
| 1/17/03 6:05 | 59.897 | Midlothian #1 tripped (223 MW) during Ramp | N/A | N/A | N/A |
| 1/20/03 5:53 | 60.108 |  | 1015 | -905 (Decreasing) | Increasing |
| 1/21/03 10:40 | 59.864 | WA Parrish tripped (690 MW) | N/A | N/A | N/A |
| 1/23/03 6:21 | 59.896 |  | -1130 | 450 (Increasing) | Increasing |
| 1/23/03 12:37 | 59.880 | Odessa Ector Plant lost (805 MW Total) | N/A | N/A | N/A |
| 1/28/03 22:13 | 59.894 |  | -135 | -635(Increasing) | Decreasing |
| 1/29/03 5:52 | 60.113 | VDI issued to lower generation by 200MW. | 1160 | -921 (Constant) | Increasing |
| 1/29/03 6:05 | 59.888 | VDI issued to raise generation by 300MW. | -810 | -313 (Increasing) | Increasing |

# Locations and Relative Activity of Congestion Management

*Days of units purchased for some time in the area described.  Data taken from daily reports and is approximate.  For global overview purposes only.

New Procedures/ Forms/ Operations Bulletins

1.  Revised the VDI Form in the Day Ahead, Transmission and Security and Frequency Desk sections.

A copy of this document is located at: http://www.ercot.com/AboutERCOT/PublicDisclosure/ERCOTProcedures.htm

2.  Realignment of Day-Ahead desk duties. (TCN #11)

3.  Revised DC-Tie section of the Operating Procedure Manual.  (TCN #12)

A copy of this document is located at: http://www.ercot.com/AboutERCOT/PublicDisclosure/ERCOTProcedures.htm

4.  Implementation of State Estimator in the Transmission and Security Desk section.  Implementation of

SFT Runs in the Day-Ahead, Operating Period and Transmission & Security desks.  (TCN #13)

5.  No new Market Operations Bulletins or procedures posted.  Power Operations Bulletins #12 and #13

were posted which outline the above changes.

Security Alert Stage/ Threatcon/ Related issues

Threatcon LOW maintained throughout January.

Describe each EECP Occurrence

No EECP throughout January.

OCN, Advisory, Alert, Energy Notice and Major Disturbances

1/3 0:700 – 08:30 	Alert issued.  Valley import limit exceeded with no available resources to mitigate the loading.

1/15 11:32  		OCN issued from 12:00 1/16 to 12:00 1/18 due to forecasted freezing

temperatures in ERCOT.

1/17 13:42		Alert issued for loss of MOI and Portal (13:45 – 14:00).

1/21 17:17		OCN issued from 1/21 to 1/24 due to forecasted freezing temperatures and gas

curtailments in ERCOT.

1/24  07:27 - 14:21	Issued Alert for an Operation Constraint for congestion on Polk – Hall Acres.

1/28 07:08 - 13:00	Issued Alert for an Operation Constraint for congestion on the Valley Import.

Major Weather Related Power System Problems

None.

Significant Communication Problems

None.

Major Computer Systems Problems/ Fixes

1/17   Held interval 13:45 – 14:00.  MOI and Portal down.

1/27   Held interval 11:30 – 12:30.  MOI and Portal down.

Major system Voltage problems

None

Blackout/Load Shed incidences

1/8 22:02   Approximately 160 MW interruptible load tripped during large schedule change.

ERCOT peak for last month (Unofficial)

1/24   08:00	44,732  (from Daily Operations Report)

Update on New Generation

Brazos Valley Energy (APX) approved for initial synchronization for 31 January.

Max / Min Temperature

1/24 	Abilene		14 °F

1/9 	ERCOT		82 °F

# New SPS & RAP’s

1/06	Special Protection System for Kendall 345/138 kV transformer (LCRA).

Other

1/1     Held interval IE 04:15 for 04:30 due to bad offset.

1/9     Held interval IE 12:30.  Constraint issue, resumed 13:00.

1/18   Held interval 15:15 – 15:30 due to bad offset.

1/21   Held interval 00:00 – 00:15 due to bad offset.