ERCOT Operations Report

ROS & OWG

For February 2003

Frequency control issues (High or Low Frequency) 59.9 > F > 60.1

| Time | Frequency | Event | Load | Reg | SCE |
| --- | --- | --- | --- | --- | --- |
| 2/1/2003 23:09 | 60.102 |  | Decreasing | 16(Decreasing) | 193 |
| 2/4/2003 17:01 | 60.120 | Bad Offset | Increasing | -750(Decreasing) | 329 |
| 2/5/2003 23:01 | 59.855 | DC TIE Tripped. | N/A | N/A | N/A |
| 2/7/2003 11:22 | 59.897 | 2 Units at the same station tripped; approximately 500 MW. | N/A | N/A | N/A |
| 2/7/2003 22:03 | 59.887 |  | Decreasing | 1000(Increasing) | -1021 |
| 2/10/2003 13:51 | 60.111 | Fail over at 13:45, SCE (Calculated) not responding after fail over | Constant | -30(Decreasing | -164 |
| 2/12/2003 6:02 | 59.853 | Several OOME instruction this period | Increasing | 350(Increasing) | -1484 |
| 2/12/2003 13:14 | 59.802 | 740 MW Unit tripped. | N/A | N/A | N/A |
| 2/14/2003 5:53 | 60.117 | >.1 Hz for 5 minutes | Increasing | -1100(Constant) | 636 |
| 2/17/2003 21:04 | 59.894 |  | Constant | -260(Increasing) | -904 |
| 2/21/2003 19:20 | 59.813 | 770 MW Unit trip. | N/A | N/A | N/A |
| 2/21/2003 19:28 | 60.164 | Overshoot recovering from unit trip. | N/A | N/A | N/A |
| 2/24/2003 6:03 | 59.865 | 2 separate unit trips around 05:45 | Increasing | 330(Constant) | -1677 |
| 2/24/2003 9:26 | 59.897 | At 08:39 a total of 1350 MW was OOME down for the NE TEX outage | Constant | 785(Constant) | -179 |
| 2/24/2003 22:24 | 59.889 | 360 MW Unit Trip | N/A | N/A | N/A |
| 2/25/2003 6:11 | 59.854 | >.1 Hz for 7 minutes. QSE reports of being short of gas. | Increasing | -100(Increasing) | -3351 |
| 2/25/2003 11:24 | 59.885 |  | Constant | 850(Constant) | -861 |
| 2/25/2003 11:49 | 59.82 | >.1 Hz for 13 minutes. EECP Declared. SRB G1,G2,G3,G4 tripped due to gas curtailments over 20 seconds, 700 total MW lost. | Constant | 850(Constant) | -1621 |
| 2/25/2003 21:56 | 60.104 |  | Decreasing | -1390(Constant) | 1092 |
| 2/25/2003 23:03 | 60.121 | >.1 Hz for 10 minutes, 2 VDI’s issued. | Decreasing | -1460(Constant) | 1747 |
| 2/25/2003 23:35 | 59.8651 | >.1 Hz for 10 minutes. Above VDI’s were ended at IE 23:30 | Decreasing | 740(Constant) | -1049 |
| 2/26/2003 22:02 | 59.891 | QSE with –110 SCE | Decreasing | -450(Increasing) | -811 |
| 2/27/2003 8:05 | 59.898 |  | Constant | -50(Increasing) | -574 |
| 2/27/2003 22:10 | 60.102 | ### QSE with +175 SCE | Decreasing | 400(Decreasing) | 616 |
| 2/28/2003 21:34 | 60.107 | QSE SCE +250 - + 687 for over 20 min. SCE Data Failed to –893 from 21:15 to 21:45. When the value returned it was +365 | Decreasing | -680(Decreasing) | -893** |
| 2/28/2003 21:52 | 60.172 | Out of REG down, VDI of 400 MW issued | Decreasing | -1350(Constant) | 394 |

# Locations and Relative Activity of Congestion Management

*Days of units purchased for some time in the area described.  Data taken from daily reports and is approximate.  For global overview purposes only.

New Procedures/ Forms/ Operations Bulletins

2/13	Operations Bulletin 14 posted.  Revisions made to Day – Ahead and Transmission Security sections of the Operating Procedure Manual.

Security Alert Stage/ Threatcon/ Related issues

2/7  19:00     ERCOT raised to Threatcon Medium Modified.

2/27 11:15    Lowered to Threatcon Low.  During the Threatcon Medium Alert level Stage, ES-ISAC raised

from Eleveated (Yellow) to High (Orange)

.

Describe each EECP Occurrence

2/25 12:01 – 19:30	EECP step 1 declared.  All QSE's were requested to bring any available generation on line and bid into the balancing market.  Terminated at 19:30.

OCN, Advisory, Alert, Energy Notice and Major Disturbances

2/3          Alert issued 12:25 due to Valley Congestion; released at 22:00.

2/6         Cold weather advisory issued at 10:11.

2/13        OCN issued for exceeding Valley import limit.

2/15	At 23:57 a Market Advisory for IE 10:00 – 16:00 and 21:00 – 23:00 due to insufficient UBES bids for 2/16  (Sunday).  The Advisory was removed at 03:00 when the market adjusted and sufficient bids were received.

2/16 	At 18:02 a Market Advisory for IE 010:00 – 12:00 due to insufficient UBES bids for 2/17.  The Advisory was removed at 02:00 when the market adjusted and sufficient bids were received.

2/17 	Issued OCN at 15:48 to announce the planned implementation of several market improvements between 18:45 and 20:00 which had the potential to cause problems with the Balancing Energy Market during the upgrade.   A second OCN was issued at 17:00 to announce that the upgrade had been cancelled.

2/24	OCN issued at 11:00 for operating day 2/25 due to expected weather and gas curtailments.

2/24	Advisory issued at 11:00 for operating day 2/25 due to expected weather and gas curtailments.

2/24	Transmission Alert issued at 18:10.  Morgan – East interface exceeded post contingency limit..

2/25	Advisory issued at 02:45 due to expected weather and gas curtailments.

2/25      Advisory issued at 03:18 due to insufficiency of UBES bids 06:00 – 08:00.

2/25       Transmission Alert issued at 07:00 – 12:00 .  Morgan – East interface exceeded post contingency limit.

2/25	Advisory issued at 07:30 requesting additional UBES bids.

2/25	At 22:36 ERCOT issued a cold weather Alert starting at 23:00  through 2/26 at 10:00.  Expected freezing rain and temperatures in the 20’s in Dallas, San Antonio, Austin, and Abilene.

2/25      Transmission Alert issued at 22:36 due to operating above first contingency transmission limits starting 23:00 2/25/03 through 10:00 2/26/03.

2/26	Alerts issued from 23:00 – 10:00 2/27 for cold weather and operating above first contingency limits.

Major Weather Related Power System Problems

2/25	Cold Weather and associated gas curtailments resulted in insufficient resources  on February 25th.

Significant Communication Problems

None.

Major Computer Systems Problems/ Fixes

2/28 	Held intervals 20:00 – 21:30 due to MOI/ Portal being inoperable.

Major system Voltage problems

None

Blackout/Load Shed incidences

2/12   13:14    168 MW interruptible load tripped due to frequency spike.

2/21   19:20    168 MW interruptible load tripped due to frequency spike.

ERCOT peak for last month (Unofficial)

2/25   19:00	42,869 (from Daily Operations Report)

Update on New Generation

No new generation approved for initial synchronization for February.

Max / Min Temperature

2/3    87 F (Corpus)

2/8    18 F (Abilene)

# New SPS & RAP’s

## Other

2/6	12:15 Deployments held through 12:30.

2/14        07:45 Deployments held through 08:00.

Limit Violations

| Transfer | Start Time | End Time | ##### Time Over Limit | Limit | Max Flow |
| --- | --- | --- | --- | --- | --- |
| Valley Import | 2/7/2003 18:41 | 2/7/2003 22:30 | 3:49 | 620 | 730 |
| Valley Import | 2/8/2003 9:22 | 2/8/2003 12:55 | 3:33 | 620 | 785 |
| Valley Import | 2/10/2003 7:26 | 2/10/2003 7:59 | 0:33 | 620 | 737 |
| East - West (Graham West) | 2/11/2003 0:25 | 2/11/2003 0:57 | 0:32 | 665 | 718 |
| East - West (Graham-West) | 2/11/2003 1:42 | 2/11/2003 2:16 | 0:34 | 665 | 687 |
| Valley Import | 2/13/2003 12:18 | 2/13/2003 17:18 | 5:00 | 620 | 704 |
| Valley Import | 2/13/2003 18:17 | 2/13/2003 22:59 | 4:42 | 620 | 694 |
| Valley Import | 2/14/2003 11:38 | 2/14/2003 20:25 | 8:47 | 620 | 704 |
| Sandow - Temple | 2/16/2003 13:36 | 2/16/2003 14:33 | 0:57 | 820 | 923 |
| Sandow – Temple | 2/18/2003 8:33 | 2/18/2003 9:05 | 0:31 | 860 | 943 |
| Sandow - Temple | 2/24/2003 6:06 | 2/24/2003 7:05 | 0:59 | 860 | 1177 |
| West - East (Morgan - East) | 2/24/2003 17:51 | 2/24/2003 21:02 | 3:11 | 840 | 1189 |
| West - East (Morgan - East) | 2/25/2003 6:44 | 2/25/2003 8:25 | 1:41 | 840 | 989 |
| West - East (Morgan - East) | 2/25/2003 18:32 | 2/25/2003 19:18 | 0:46 | 840 | 944 |
| Sandow - Temple | 2/27/2003 17:23 | 2/27/2003 18:05 | 0:42 | 725 | 776 |