COMPLIANCE REPORT TO ROS

March 11, 2003

- Protocol-Based Compliance Enforcement:  In the upcoming Operations Seminar, Compliance will present issues on Protocol compliance problems with market participants that start from the Operating Desks.

- ERCOT Frequency Control Related Issues:

  - Single Control Area CPS 1 Performance (1 minute average deviation) for February fell to 121 due to cold weather problems around the EECP.  It remains above 100 needed for passing.

  - Work continues to fix problems with QSE AS reports.  Again, some Protocol revisions are needed to update exclusions from AS reporting.

  - PDCWG will have discussed proposals for new NERC “Balancing” standards now in draft at its March 10 meeting.   These standards have not been released by NERC for comment yet, but the comment period will be relatively short (30 days).

  - PRR 350 eliminates the 3 point smoothing algorithm and takes affect March 19.  This should have a positive impact on frequency control; initial reports to follow in April.

- Transmission Security Issues:

  - NERC posted the draft standard for “Operating within Limits”.   Ellis Rankin from Oncor is participating in this group.  Comments are due by APRIL 2.  All are encouraged to comment – even if just to concur with the proposed standard.

  - Steve Myers of ERCOT Operations is part of a NERC group to examine definition issues for transmission security operating limit violations.   Steve is leading the effort to blend this work into the above standard.   Thanks, Steve!

  - Related  to the above, John Adams of ERCOT Operations has reviewed the contingency list and will discuss which situations have severe 1st contingency consequences – that is, system stability issues, cascading outages, or voltage collapse.

  - CSC violations will be reported to ROS, and NERC, until John Adams work in c) above is completed.  Performance in February (draft) :  3 West-East violations, 6 South-North, O South-Houston. Operations/TO validation needed.

- NERC Compliance program for 2003

  - Tabulation for 2002 results is attached.   Other measures not reported to NERC had minor problems.  ERCOT Security violations were the largest issue.  ERCOT control violations were removed by NERC waiver for CPS2 and retroactive change to CPS1 bandwidth (epsilon 1).   Lateness with reporting, and questionable understanding of obligations, were also issues, particularly with smaller TDSP’s.

  - Most NERC 2003 measures will be, again, self-certified.  Forms will be posted and emailed in May. Several TO’s and QSE’s will be visited; two are in progress now.

  - These measures will be assessed in 2003 that involve Regional procedures:

    - SSWG procedures describing steady state data requirements

    - DWG procedures describing dynamics data requirements

    - Disturbance monitor location requirements from SPWG (in Operating Guides)

  - ERCOT Compliance will be audited by NERC on March 25 for 2002 program.

  - NERC compliance organization proposal will be posted for comment in late March.

- Control Center Backup plans were due to ERCOT on 2/28/03 per new Operating Guides requirement.   Operations will be reviewing them in March.

- 2003 Underfrequency load shed survey of TDSP’s will be April 23th at 9:00-10:00  am.