ERCOT Operating Guides

Section 7:  Planning Criteria, Disturbance Monitoring and System Protection

Contents

7	Planning Criteria, Disturbance Monitoring and 
System Protection	7-3

7.1	Planning Criteria	7-3

7.1.1	Introduction	7-3

7.1.2	Load Forecasts	7-3

7.1.3	Resource Capability	7-4

7.1.4	Transmission Reliability Testing	7-4

7.1.5	Reports Of Testing	7-5

7.1.6	System Modeling Information	7-5

7.1.7	ERCOT Clarifications and Definitions of NERC Planning Standards
 Contingency Types C and D	7-11

7.2	Disturbance Monitoring Requirements	7-13

7.2.1	Introduction	7-13

7.2.2	Fault Recording Equipment	7-13

7.2.3	Dynamic Disturbance Recording Equipment	7-16

7.2.4	Equipment Reporting Requirements	7-16

7.2.5	Review Process	7-16

7.3	System Protective Relaying	7-17

7.3.1	Introduction	7-17

7.3.2	Design and Operating Requirements for ERCOT System Facilities	7-17

7.3.3	Performance Analysis Requirements for ERCOT System Facilities	7-19

7.3.4	Maintenance and Testing Requirements for ERCOT System Facilities	7-21

7.3.5	Requirements and Recommendations for ERCOT System Facilities	7-21

7.4	Document Control	7-32

# Planning Criteria, Disturbance Monitoring and System Protection

## 7.1	Planning Criteria

### 7.1.1	Introduction

The Electric Reliability Council of Texas (ERCOT) power system consists of those generation and transmission facilities (60 kV and higher voltages) which are controlled by individual ERCOT market participants and which function as part of an integrated and coordinated power supply network.  Each reference in this document to ERCOT market participants includes Generation Resources (GRs), Qualified Scheduling Entities (QSEs), Competitive Retailers (CRs), Transmission/Distribution Service Providers (TDSPs), and other that use the transmission system.

In order to maintain reliable operation of the ERCOT power system, it is necessary that all ERCOT market participants observe and subscribe to certain minimum planning criteria. The criteria set forth herein, combined with the NERC Planning Standards, constitute these minimum-planning criteria. Tests outlined herein shall be performed to determine conformance to these minimum criteria; however, because ERCOT recognizes that events more severe than those outlined in these criteria could cause separation, other tests may also be performed if necessary for information purposes.

The complexity and uncertainty inherent in the planning and operation of the ERCOT power system make exhaustive testing impracticable; therefore, to gain maximum benefit from the limited number of tests which are performed, the selection of the specific tests and the frequency of their performance will be made solely upon the basis of the expected value of the reliability information obtainable from the test.

It is the responsibility of each ERCOT TDSP to perform tests appropriate to ensure the reliability of its own transmission facilities, and to recommend for further study by the ERCOT system planning function (SPF) or the ERCOT Reliability Operations Subcommittee (ROS) tests, which examine effects of importance to multiple ERCOT TDSPs or the ERCOT power system.  Upon consideration of such recommendations, the ERCOT SPF and the ERCOT ROS shall coordinate the performance of tests as necessary to assess the reliability of the planned ERCOT power system.

The ERCOT Planning Assessment and Review Working Group (PARWG) will review the ERCOT Planning Criteria every three years to ensure it meets the requirements in the NERC Planning Standards.  PARWG will periodically review the planning criteria, procedures, and practices of individual ERCOT TDSPs to insure consistency with NERC and ERCOT criteria.

### 7.1.2	Load Forecasts

Each ERCOT DSP directly interconnected with the transmission system (or its agent so designated to ERCOT) shall provide annual load forecasts to the ERCOT SPF as outlined in the ERCOT Annual Load Data Request (ALDR) Procedures. For each substation not owned by either a TSP or a DSP, the owner shall provide a substation load forecast to the directly-connected TDSP sufficient to allow it to adequately include that substation in its ALDR response.

### 7.1.3	Resource Capability

ERCOT will periodically determine the minimum reserve margin required to ensure the adequacy of installed generation capability in ERCOT. ERCOT or the Public Utility Commission of Texas may also approve specific market participant requirements to ensure that the required minimum reserve margin is maintained.

The ERCOT SPF maintains a database containing existing and proposed generating capability historical and projected values for demand and energy; and proposed major transmission system additions.  This database is updated periodically and the Capacity Demand Reserve (CDR) Working Paper is produced annually.

### 7.1.4	Transmission Reliability Testing

The interconnection philosophy of ERCOT is to minimize loss of load by remaining interconnected.  Interconnected system planning will include steady state and dynamic simulated testing by ERCOT TDSPs and the ERCOT SPF to represent specific occurrences for each type of contingency specified below or listed in Table I of the NERC Planning Standards. Table I of the NERC Planning Standards is included in this document for reference.  Also included are ‘ERCOT Clarifications and Definitions’ which are applicable to testing for NERC Planning Standards contingency types C and D.

The contingency tests will be performed for reasonable variations of load level, generation schedules, planned transmission line maintenance outages, and anticipated power transfers.  At a minimum, this should include projected loads for the upcoming summer and winter seasons and a five-year planning horizon.  The ERCOT TDSPs involved should plan to resolve any unacceptable test results through the provision of transmission facilities, the temporary alteration of operating procedures (Remedial Action Plans), temporary Special Protection Systems, or other means as appropriate.

While the requirements listed in Table I address most ERCOT planning concerns, tests will also be conducted to ensure that the planned system conforms to the following additional requirements:

1.	The contingency loss of a double-circuit transmission line that exceeds 0.5 miles in length (either without a fault or subsequent to a normally-cleared non-three-phase fault) with all other facilities normal should not cause a) cascading or uncontrolled outages, b) instability of generating units at multiple plant locations, or c) interruption of service to firm demand or generation other than that isolated by the double-circuit loss, following the execution of all automatic operating actions such as relaying and special protection systems. Furthermore, the loss should result in no damage to or failure of equipment and, following the execution of specific non-automatic predefined operator-directed actions (i.e., Remedial Action Plans), such as generation schedule changes or curtailment of interruptible load, should not result in applicable voltage or thermal ratings being exceeded.

2.	With any single generating unit unavailable, and with any other generation preemptively redispatched, the contingency loss of a single transmission element (either without a fault or subsequent to a normally-cleared non-three-phase fault) with all other facilities normal should not cause a) cascading or uncontrolled outages, b) instability of generating units at multiple plant locations, or c) interruption of service to firm demand or generation other than that isolated by the transmission element, following the execution of all automatic operating actions such as relaying and special protection systems. Furthermore, the loss should result in no damage to or failure of equipment and, following the execution of specific non-automatic predefined operator-directed actions (i.e., Remedial Action Plans) such as generation schedule changes or curtailment of interruptible load, should not result in applicable voltage or thermal ratings being exceeded.

The ERCOT SPF is responsible for gathering load data, for use in the ERCOT load flow cases via the ALDR.  The ERCOT ROS coordinates with the ERCOT SPF in the performance of steady state and dynamic simulation testing of the bulk power system to determine the impact on the planned system of occurrences of the types of contingencies listed in the NERC Planning Standards.  The Steady State Working Group (SSWG), Dynamics Working Group (DWG) and System Protection Working Group (SPWG) work with the ERCOT SPF to create databases and perform tests as outlined in these criteria.

These databases created by the ERCOT ROS Working Groups are available for use by ERCOT market participants.  It is the responsibility of the individual ERCOT TDSPs to use these databases to perform steady state and dynamic tests appropriate to evaluate the compliance of their transmission facilities with the ERCOT Planning Criteria and to recommend, for further study by ERCOT, tests, which examine effects of importance to multiple ERCOT TDSPs or the ERCOT bulk power system.  Such tests are discussed by the ERCOT ROS and the ERCOT SPF and are subsequently performed under the direction of the ERCOT SPF or the ERCOT ROS as appropriate.  The individual TDSPs affected by identified issues will pursue appropriate solutions.

### 7.1.5	Reports Of Testing

The ERCOT SPF annually directs the preparation of the section of the EIA-411 Report requested by the Department of Energy which addresses the adequacy of the ERCOT bulk power system as well as input to various NERC reports. Studies performed by ERCOT and comments by the individual TDSPs regarding tests that they have performed provide the basis for statements concerning the adequacy of the planned ERCOT system.

### 7.1.6	System Modeling Information

Information on existing and future ERCOT system components and topology is necessary for ERCOT to create databases and perform tests as outlined in these criteria.  To ensure that such information is made available to ERCOT, the following actions by ERCOT market participants are required:

1.	Each TDSP, or its designated agent, shall provide accurate modeling information for all ERCOT transmission facilities owned or planned by the TDSP.  The information provided shall include, but not be limited to, the following:

a.	Information necessary to represent the TDSP’s transmission facilities in any model of the ERCOT transmission system whose creation has been approved by ERCOT, including modeling information detailed in procedures of the SSWG, DWG, and SPWG; and

b.	Identification of a designated contact person responsible for providing answers to questions ERCOT may have regarding the information provided.

Further, each TDSP owning or planning transmission facilities shall attend the scheduled meetings and otherwise participate in the activities of the SSWG and the SPWG, unless specifically exempted from these activities by ERCOT.

2.	Each GR, or its designated agent, shall provide accurate modeling information for each existing or publicly-announced ERCOT generating unit for which it is the majority owner. The information provided shall include, but not be limited to, the following:

a.	Information necessary to represent the GR’s generation and interconnection facilities in any model of the ERCOT electrical system whose creation has been approved by ERCOT, including modeling information detailed in procedures of the SSWG, DWG, and SPWG; and

b.	Identification of a designated contact person responsible for providing answers to questions ERCOT may have regarding the information provided.

Typical or representative information may be provided for planned facility additions or modifications, but such information shall be revised using actual design or construction information once it becomes available.  All information provided shall be provided on the schedule and in the format specified by ERCOT, and shall exclude Protected Information as described in the Protocols.

Table I. Transmission Systems Standards — Normal and Contingency Conditions

| Category | Contingencies |  | System Limits or Impacts |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Initiating Event(s) and Contingency Component(s) | Components Out of Service | Thermal Limits | Voltage Limits | System Stable | Loss of Demand or Curtailed Firm Transfers | Cascadingc Outages |
| A – No Contingencies | All Facilities in Service | None | Normal | Normal | Yes | No | No |
| B – Event resulting in the loss of a single component. | Single Line Ground (SLG) or 3-Phase (3Ø) Fault, with Normal Clearing: 1. Generator 2. Transmission Circuit 3. Transformer Loss of a Component without a Fault. | Single Single Single Single | Applicable Rating a (A/R) A/R A/R A/R | Applicable Rating a (A/R) A/R A/R A/R | Yes Yes Yes Yes | No b No b No b No b | No No No No |
|  | Single Pole Block, Normal Clearing: 4. Single Pole (dc) Line | Single | A/R | A/R | Yes | Nob | No |
| C – Event(s) resulting in the loss of two or more (multiple) components. | SLG Fault, with Normal Clearing: 1. Bus Section 2. Breaker (failure or internal fault) | Multiple Multiple | A/R A/R | A/R A/R | Yes Yes | Plannedd Plannedd | No No |
|  | SLG or 3Ø Fault, with Normal Clearing, Manual System Adjustments, followed by another SLG or 3Ø Fault, with Normal Clearing: 3. Category B (B1, B2, B3, or B4) contingency, manual system adjustments, followed by another Category B (B1, B2, B3, or B4) contingency | Multiple | A/R | A/R | Yes | Plannedd | No |
|  | Bipolar Block, with Normal Clearing: 4. Bipolar (dc) Line Fault (non 3Ø), with Normal Clearing: 5. Double Circuit Towerline | Multiple Multiple | A/R A/R | A/R A/R | Yes Yes | Plannedd Plannedd | No No |
|  | SLG Fault, with Delayed Clearing: 6. Generator 8. Transformer 7. Transmission Circuit 9. Bus Section | Multiple Multiple | A/R A/R | A/R A/R | Yes Yes | Plannedd Plannedd | No No |
| D e – Extreme event resulting in two or more (multiple) components removed or cascading out of service | 3Ø Fault, with Delayed Clearing (stuck breaker or protection system failure): 1. Generator 3. Transformer 2. Transmission Circuit 4. Bus Section 3Ø Fault, with Normal Clearing: 5. Breaker (failure or internal fault) Other: 6. Loss of towerline with three or more circuits 7. All transmission lines on a common right-of way 8. Loss of a substation (one voltage level plus transformers) 9. Loss of a switching station (one voltage level plus transformers) 10. Loss of a all generating units at a station 11. Loss of a large load or major load center 12. Failure of a fully redundant special protection system (or remedial action scheme) to operate when required 13. Operation, partial operation, or misoperation of a fully redundant special protection system (or remedial action scheme) for an event or condition for which it was not intended to operate 14. Impact of severe power swings or oscillations from disturbances in another Regional Council. | Evaluate for risks and consequences.  May involve substantial loss of customer demand and generation in a widespread area or areas.  Portions or all of the interconnected systems may or may not achieve a new, stable operating point.  Evaluation of these events may require joint studies with neighboring systems.  Document measures or procedures to mitigate the extent and effects of such events.  Mitigation or elimination of the risks and consequences of these events shall be at the discretion of the entities responsible for the reliability of the interconnected transmission systems. |  |  |  |  |  |

Footnotes to Table I.

- a)	Applicable rating (A/R) refers to the applicable normal and emergency facility thermal rating or system voltage limit as determined and consistently applied by the system or facility owner.

- b)	Planned or controlled interruption of generators or electric supply to radial customers or some local network customers, connected to or supplied by the faulted component or by the affected area, may occur in certain areas without impacting the overall security of the interconnected transmission systems. To prepare for the next contingency, system adjustments are permitted, including curtailments of contracted firm (non-recallable reserved) electric power transfers.

- c)	Cascading is the uncontrolled successive loss of system elements triggered by an incident at any location. Cascading results in widespread service interruption, which cannot be restrained, from sequentially spreading beyond an area predetermined by appropriate studies.

- d)	Depending on system design and expected system impacts, the controlled interruption of electric supply to customers (load shedding), the planned removal from service of certain generators, or the curtailment of contracted firm (non-recallable reserved) electric power transfers may be necessary to maintain the overall security of the interconnected transmission systems.

- e)	A number of extreme contingencies that are listed under Category D and judged to be critical by the transmission planning entity(ies) will be selected for evaluation. It is not expected that all possible facility outages under each listed contingency of Category D will be evaluated.

### 7.1.7	ERCOT Clarifications and Definitions of NERC Planning Standards Contingency Types C and D

#### 7.1.7.1	Category C

Initiating Event and Contingency Component Definitions:

"Bus Section" shall be interpreted to mean any section of buswork, which would be isolated by normal relay/breaker operation when faulted.

"Manual System Adjustments" shall be interpreted to include only operator actions which a) would be made not later than 1 hour after clearing of the first fault, b) are made using remote control capability or communications with other operators having such capability, c) include circuit switching, changes in the schedules of generating units operating at clearing of the first fault, and changes in the schedules of other generating units which can contribute within 1 hour, and d) exclude the physical repair or replacement of damaged equipment and the starting of any generating unit which cannot contribute within 1 hour.

Planned Loss of Demand or Curtailed Firm Transfer Definition:

All load interruption, generator tripping, or generation schedule changes must be either automatic or prearranged (with associated written operating procedures).  Actions must be executable in time to avoid any equipment damage or safety violations, but in any case within 30 minutes of fault clearing.

Cascading Outage Definition:

Cascading outages are defined as the uncontrolled loss of any system facilities or load, whether because of thermal overload, voltage collapse, or loss of synchronism, except those occurring as a result of fault isolation.

Implementation Guidelines:

Equipment ratings and permissible voltage levels shall be determined by the facility owner with the concurrence of the ERCOT SPF.

Evaluation of all the possible combination of facility outages under Category C is not required. Each TDSP with bulk transmission facilities will evaluate one or more Category C contingencies annually.  The contingencies selected may be based on the results of related studies or actual events and which, in the engineering judgment of the facility owner, the ERCOT SPF or any TDSP, may have unacceptable consequences.

#### 7.1.7.2	Category D:

Large Load or Major Load Center Definition:

A large load or major load center shall be defined as a large single load or a group of electrically close loads comprising a peak load of between 50 and 500 MW.  Loss of this load or load center will not include any other system elements other than those directly connected to the lost load.

Evaluation Implementation:

Evaluations of Category D contingencies are not required to be performed annually.  Evaluations should be performed for the following:

- Contingencies previously studied for which the conditions assumed in the study have changed significantly and which may adversely affect the results of the study.

- Contingencies not previously studied that, based on the results of related studies or actual events may in the engineering judgment of the facility owner, the ERCOT SPF or any TDSP, have unacceptable consequences.

## 7.2	Disturbance Monitoring Requirements

### 7.2.1	Introduction

Disturbance monitoring is necessary to determine:

- The performance of the ERCOT system,

- The effectiveness of protective relaying systems,

- Verify ERCOT system models, and

- Determine the causes of ERCOT system disturbances (unwanted trips, faults, and protective relay system actions).

To ensure that adequate data is available for these activities, the disturbance monitoring requirements and procedures discussed in this document have been established by ERCOT for Facility Owners in the ERCOT system.

Disturbance monitoring equipment includes digital fault recorders (DFRs), certain protective relays with fault recording capability, and dynamic disturbance recorders (DDRs). Sequence-of-event recorders (SERs), although considered equipment to monitor disturbances, are not preferred devices, as they provide limited information.  SERs have been replaced by digital fault recorders and microprocessor-based protective relays.

### 7.2.2	Fault Recording Equipment

Fault recording equipment includes digital fault recorders (DFRs) and protective relays with fault recording capability that meet the triggering requirements below.  Fault recording equipment should be time synchronized when practical.

#### 7.2.2.1	Triggering Requirements

Fault recording equipment triggering must occur for system voltage magnitude and current magnitude disturbances (delta V and delta I) without requiring any circuit breaker operations or trip outputs from protective relay systems. Triggering by additional methods is acceptable. Triggering shall be adjusted to operate for faults in the area to be monitored, which should overlap into the area of coverage of adjacent fault recorders.

#### 7.2.2.2	Location Requirements

The location criteria below shall apply to equipment operated at or above 60 kV. The Facility Owner shall install minimum fault recording equipment at the following facilities:

- Interconnections to other Regions (i.e. outside ERCOT).

- Switching stations where electrical transfers of equipment can be made between ERCOT and another Region.

- Switching stations having three or more non-radial 345 kV line terminals.  If a switching station is one bus removed from a station with a larger number of line terminals, then the fault recorder shall be located at the larger station and not required at the smaller station.

- Switching stations that are more than one bus controlled by breakers, away from a fault recorder and have five or more non-radial line terminals.

- For the purpose of evaluating #c. and #d. in this section, autotransformer or generating capacity totaling 150 MVA or greater (based upon minimum nameplate rating upon which transformer impedance is stated, i.e., base rating) shall constitute a non-radial line terminal at the highest voltage level to which it is directly connected.

- All generating station switchyards connected to the ERCOT System with a generating capacity above 100 MVA.

All fault recording equipment shall be either DFR’s or fault recording protective relays

#### 7.2.2.3	Data Recording Requirements

The following quantities must be recorded for equipment operating at 60 kV or above at facilities where fault recording equipment is required:

- Two sets of voltages for breaker-and-a-half and ring bus substation configurations.  One set of voltages for each bus in other substation configurations.  A set of voltages shall consist of each phase voltage waveform and the residual voltage waveform.

- For all lines, neutral (residual) current waveform.

- Circuit breaker status.

- Circuit breaker trip circuit status.

- Date and time stamp (CST).

For all new or upgraded fault recorder installations, additional items must also be recorded, as follows:

- For all autotransformers, current waveform for three phases and either neutral / residual current waveform or current waveform in delta windings.

- For all lines, two phase current waveforms.

- Status – carrier transmitter control, i.e. start, stop, keying.

- Status – carrier received.

#### 7.2.2.4	Data Reporting Requirements

The Facility Owner shall report all fault data to ERCOT at least annually as follows:

- All 345 kV system faults.

- When multiple recorders exist for a single event, data from the best recording (usually the closest recorder) is required.

This data shall be submitted in the form of a computer file or files. Two formats are acceptable for data submissions. One format shall be COMTRADE fault recordings (.cfg and .dat files) and one or more associated text files that associate the COMTRADE recordings with system disturbances and ERCOT short circuit database bus numbers. The second format shall be a Microsoft Excel spreadsheet or comma delimited ASCII text that can be read into a Microsoft Excel spreadsheet. For this second format, the data fields to be reported for each record, in the following order, are:

#### Reporting Entity

| Faulted Circuit | Circuit or Bus (1, 2, A, B, N, S, etc.) |  |
| --- | --- | --- |
| From Bus (ERCOT short circuit database bus number) |  |  |
|  | To Bus (ERCOT short circuit database bus number) |  |
| Nominal Voltage of Faulted Branch or Bus (kV) |  |  |
| Physical Fault Location in Percent from “From Bus” (if physical location found, i.e. not calculated location) |  |  |
|  |  | Date (CST, MM/DD/YYYY) |
|  |  | Time (CST, HH:MM:SS, 24 hour format) |
|  |  | Cause Code |
| Fault Recorder Data |  | Circuit (1, 2, A, B, N, S, etc.) |
| From Bus – Recorder Location (ERCOT short circuit database bus number) |  |  |
|  | To Bus – Monitored branch (ERCOT short circuit database bus number) |  |
|  | Nominal Voltage of Monitored Branch (kV) |  |
|  | Nominal Voltage of Monitored Branch (kV) |  |
|  | Measured Current Magnitude (primary value in RMS amperes) |  |
|  | Recorded Fault Duration (cycles) |  |
|  | Fault Type (using reporting entity’s phase designations – AB, CG, etc.) |  |
| Optional Comments (40 char. max.) |  |  |

ERCOT shall compile all annual fault data into a database. This database shall be available to any ERCOT member upon their request. Data submitted will be retained by ERCOT for a minimum of one year.

Facility Owners shall provide fault records to ERCOT or NERC upon their request, along with channel identification and scaling information to allow analysis of the records. Fault records shall be retained and made available for at least one year from the date the record was made. Fault records shall be shared between Facility Owners, upon their request, for the analysis of system disturbances.

#### 7.2.2.5	Maintenance and Testing Requirements

Facility Owners shall maintain and test their Fault recording equipment as follows:

- In accordance with the manufacturer’s recommendations.

- Calibration of the analog (waveform) channels shall be performed at installation and when records from the equipment indicate a calibration problem.  Calibration can be monitored through the analysis and correlation of fault records with system models and the records of other fault recorders in the area.

- Fault recording equipment must be operationally tested at least annually to ensure that the equipment is functional.  Acceptable tests are the production of a manually triggered record (remotely or at the device), or automatic record production due to a power system disturbance.

### 7.2.3	Dynamic Disturbance Recording Equipment

Reserved

### 7.2.4	Equipment Reporting Requirements

Facility Owners shall maintain and submit the following data to ERCOT or NERC, as required:

| ACTION | TIMING |
| --- | --- |
| A current database describing the disturbance monitoring equipment installed and its location | Provide to ERCOT by October 30 each year. |
| ERCOT shall maintain a database containing this information | Update annually. |
| Each Facility Owner shall provide this information to ERCOT or NERC on their request | Within 30 days. |

The database shall include installation location; type of equipment, make and model of equipment, operational status, a listing of the major equipment being monitored and the date the equipment was last tested.

### 7.2.5	Review Process

ERCOT shall review fault recorder and disturbance recorder locations for compliance and adequacy when significant changes are made to the ERCOT system or at least every five years.

## 7.3	System Protective Relaying

### 7.3.1	Introduction

The satisfactory operation of the ERCOT System (equipment operated above 60 kV), especially under abnormal conditions, is greatly influenced by protective relay system.

Protective relay systems are defined as the total combination of:

- The protective relays,

- Associated communications system,

- Voltage and current sensing devices, and,

- The dc system up to the terminals in the circuit breaker.

Although relaying of tie points between Facility Owners is of primary concern to the ERCOT System, internal protective relay system often directly, or indirectly, affects the adjacent area also.  Facility Owners are those entities owning facilities in the ERCOT System.  Facility Owners have an obligation to implement relay application, operation, and preventive maintenance criteria that assure the highest practicable reliability and availability of service to the ultimate power consumers of the concerned area and neighboring areas.  Protective relay system of individual Facility Owners shall not adversely affect the stability of ERCOT System interconnections.  Additional minimum protective relay system requirements are outlined in NERC Planning Standards.

These objectives and design practices shall apply to all new protective relay system applied at 60 kV and above unless otherwise specified.  It is recognized that there may be portions of the existing ERCOT System that do not meet these objectives.  It is the responsibility of individual Facility Owners to assess the protective relay system at these locations and to make any modifications that they deem necessary.  Similar assessment and judgment should be used with respect to protective relay system existing at the time of revisions to this guide.  Special local conditions or considerations may necessitate the use of more stringent design criteria and practices.

### 7.3.2	Design and Operating Requirements for ERCOT System Facilities

- Protective relay system shall be designed to provide reliability, a combination of dependability and security, so that protective relay system will perform correctly to remove faulted equipment from the ERCOT System.

- For planned ERCOT System conditions, protective relay system shall be designed not to trip for stable swings which do not exceed the steady-state stability limit.  Note that when out-of-step blocking is used in one location, a method of out-of-step tripping should also be considered.  Protective relay system shall not interfere with the operation of the ERCOT System under the procedures identified in the other Operating Guides.

- Any loading limits imposed by the protective relay system shall be documented and followed as an ERCOT System operating constraint.

- The thermal capability of all protection system components shall be adequate to withstand the maximum short time and continuous loading conditions to which the associated protected elements may be subjected, even under first-contingency conditions.

- Applicable IEEE/ANSI guides shall be considered when applying the protective relay system on the ERCOT System.

- The planning and design of generation, transmission and substation configurations shall take into account the protective relay system requirements of dependability, security and simplicity.  If configurations are proposed that require protective relay systems that do not conform to this guide or to accepted IEEE/ANSI practice, then the Facility Owners affected shall negotiate a solution.

- All Facility Owners shall give sufficient advance notice to ERCOT of any changes to their facilities that could require changes in the protective relay system of neighboring Facility Owners.

- Facility Owner’s operations personnel shall be familiar with the purposes and limitations of the protective relay system.

- The design, coordination, and maintainability of all existing protective relay systems shall be reviewed periodically by the Facility Owner to ensure that the protective relay systems continue to meet ERCOT System requirements.  This review shall include the need for redundancy.  Where redundant protective relay systems are required, separate AC current inputs and separately fused DC control voltages shall be provided with the upgraded protective relay system.  Documentation of the review shall be maintained and supplied by the Facility Owner to ERCOT or NERC on their request within 30 days.  This documentation shall be reviewed by ERCOT for verification of implementation.

- Upon ERCOT’s request, within 30 days, PGCs shall provide ERCOT with the operating characteristics of any generator’s equipment protective relay system or controls that may respond to temporary excursions in voltage, frequency, or loading with actions that could lead to tripping of the generator.

- Upon ERCOT’s request, within 30 days, generation entities shall provide ERCOT with information that describes how generator controls coordinate with the generator’s short-term capabilities and the protective relay system.

- Over-excitation limiters, when used, shall be coordinated with the thermal capability of the generator field winding.  After allowing temporary field current overload, the limiter shall operate through the automatic AC voltage regulator to reduce field current to the continuous rating.  Return to normal AC voltage regulation after current reduction shall be automatic.  The over-excitation limiter shall be coordinated with the over-excitation protection so that over-excitation only operates for failure of the voltage regulator/limiter.  Documentation of coordination shall be supplied, by generation entities, to ERCOT upon their request within 30 days.

- Special Protection Systems (SPS) are protective relay systems designed to detect abnormal ERCOT System conditions and take pre-planned corrective action (other than the isolation of faulted elements) to provide acceptable ERCOT System performance.  SPS actions include among others, changes in demand, generation, or system configuration to maintain system stability, acceptable voltages, or acceptable facility loadings.  If used:

- SPS shall be automatically armed when appropriate.

- The status indication of any automatic or manual arming of SPS shall be provided as SCADA alarm inputs.

- SPS shall be designed in accordance with the intent of this Operating Guide when they are required to prevent adverse effects outside the local area.

- The owner(s) of existing, modified, or proposed SPS shall submit documentation of the SPS to ERCOT for review and compilation into an ERCOT SPS database.  The documentation shall detail the design, operation, functional testing, and coordination of the SPS with other protection and control systems.

- ERCOT shall conduct a review of proposed or modified SPS before the SPS is placed in service.  This review shall verify that the SPS complies with ERCOT and NERC criteria and guides.  The review shall include system studies verifying that failure of a single component of the SPS, which would result in failure of the SPS to operate when required, would not result in cascading transmission outages.  The review shall also verify that misoperation, incorrect operation, or unintended operation of an SPS, when considered by itself, shall meet the system performance requirements of categories A, B, and C of Table I of NERC Planning Standard I.A.  This review shall be documented and the documentation provided to NERC on request within 30 days.

- ERCOT shall conduct a review of existing SPS every five years or as required by changes in system conditions.  This review shall verify that the SPS complies with ERCOT and NERC criteria and guides.  The review shall evaluate and document the consequences of failure of a single component of the SPS, which would result in failure of the SPS to operate when required.  The review shall also evaluate and document the consequences of misoperation, incorrect operation, or unintended operation of an SPS, when considered by itself, and without any other system contingency.  If deficiencies are identified, a plan to correct the deficiencies shall be developed and implemented.  The current review results shall be kept on file and supplied to NERC on request within 30 days.

- SPS owners shall notify ERCOT of all SPS operations.  Documentation of SPS failures or misoperations shall be provided to ERCOT using Form 1 of item A.1.2 in Appendix A.  ERCOT shall conduct an analysis of all SPS operations, misoperations, and failures. If deficiencies are identified, a plan to correct the deficiencies shall be developed and implemented.

### 7.3.3	Performance Analysis Requirements for ERCOT System Facilities

- All ERCOT System disturbances (unwanted trips, faults, and protective relay system operations) shall be analyzed by the affected Facility Owner promptly and any deficiencies investigated and corrected.

- All protective relay system misoperations in systems 100 kV and above shall be documented, including corrective actions and the documentation supplied by the affected Facility Owner to ERCOT or NERC upon their request within five business days.  All protective relay system misoperations shall be documented using “Relay Misoperation Report” Form 1 (Appendix A, A1.2).  Any of the following events constitute a reportable protective relay system misoperation:

- Failure to Trip – Any failure of a protective relay system to initiate a trip to the appropriate terminal when a fault is within the intended zone of protection of the device.

- Slow Trip – A correct operation of a protective relay system for a fault in the intended zone of protection where the relay system initiates tripping slower than the system design intends.

- Unnecessary Trip During a Fault – Any relay initiated operation of a circuit breaker during a fault when the fault is outside the intended zone of protection.

- Unnecessary Trip Other Than Fault – The unintentional operation of a protective relay system, which causes a circuit breaker to trip when no system fault is present.  May be due to vibration, improper settings; load swing, defective relays, or SCADA system malfunction.

- Employee action that directly initiates a trip is not included in this category. It is the intent of this reporting process to identify misoperations of the relay system as it interrelates with the electrical system, not as it interrelates to personnel involved with the relay system. With this in mind, if an individual directly initiates an operation, it is not counted as a misoperation (i.e., unintentional operation during tests). On the other hand, if a technician leaves trip test switches or cut-off switches in an inappropriate position and a system fault or condition causes a misoperation, this would be counted as a relay system misoperation

- Failure to Reclose – Any failure of a protective relay system to automatically reclose following a fault if that is the design intent.

- All SPS misoperations shall be documented, including corrective actions and the documentation supplied to ERCOT and NERC upon request within five business days.  All SPS misoperations shall be documented using “Relay Misoperation Report” Form 1 (Appendix A, A1.2).  Any of the following events constitute a reportable SPS misoperation:

- Failure to Operate – Any failure of a SPS to perform its intended function within the designed time when system conditions intended to trigger the SPS occur.

- Failure to Arm – Any failure of a SPS to automatically arm itself for system conditions that are intended to result in the SPS being automatically armed.

- Unnecessary Operation – Any operation of a SPS that occurs without the occurrence of the intended system trigger condition(s).

- Unnecessary Arming – Any automatic arming of a SPS that occurs without the occurrence of the intended arming system condition(s).

- Failure to Reset – Any failure of a SPS to automatically reset following a return of normal system conditions if that is the design intent.

- Facility Owners shall document the performance of their protective relay system utilizing the method described in the paper “Transmission Protective Relay System Performance Measuring Methodology”, IEEE/PSRC Working Group 13 September 16, 1999. Facility Owners shall report the performance of their 345 kV protective relay system for the previous twelve months to ERCOT on an annual basis.  Reporting shall begin in November 2001, with data for the period October 01, 2000 to September 30, 2001. The performance data reported shall include the total number of protective relay system misoperations, the total number of events, and the factor “k”.

- At least annually, ERCOT shall review the protective relay system misoperation reports and 345 kV performance data of Facility Owners for analysis of protective relay system performance and compliance.

- All Facility owners shall install, maintain, and operate disturbance monitoring equipment in accordance with the requirements in Section B.2 of this Appendix.

- Facility owners shall provide an assessment of the system performance results of simulation tests of the contingencies in Table I of the NERC Planning Standard I.A.  These assessments should be based on existing protection systems and any existing backup or redundancy protection systems to determine that existing transmission protection systems are sufficient to meet the system performance levels as defined in NERC Planning Standard I.A. and the associated Table I.  All non-compliance findings shall be documented, including a plan for achieving compliance.  These assessments shall be provided to NERC or ERCOT on their request within 30 days.

### 7.3.4	Maintenance and Testing Requirements for ERCOT System Facilities

- The Facility Owner shall test and verify the operation of each new or modified protective relay system prior to placing the equipment in its zone of protection in service.

- Facility Owners shall have documented protective relay system maintenance and testing programs in place.  Documentation shall include identification of protective relay system, a summary of testing procedures including requirements for frequency of tests, and the date last tested.

- The Facility Owner shall periodically test and inspect all components of the protective relay system to assure continued reliability.  Identified deficiencies shall be corrected.  Documentation demonstrating compliance with the Facility Owner’s maintenance and testing programs shall be supplied to ERCOT or NERC upon their request within 30 days.

### 7.3.5	Requirements and Recommendations for ERCOT System Facilities

#### 7.3.5.1	General Protection Criteria

Dependability

- Except as noted in Sections 4 and 5 below, all elements of the ERCOT System operated at 100 kV and above (i.e., lines, buses, transformers, generators, breakers, capacitor banks, etc.) shall be protected by two protective relay systems.  Each protective relay system shall be independently capable of detecting and isolating all faults thereon.

- The protective relay system design should avoid the use of components common to the two protective relay systems.  Areas of common exposure should be kept to a minimum to reduce the possibility of both protective relay systems being disabled by a single contingency.

- The use of two identical protective relay systems is not generally recommended, due to the risk of simultaneous failure of both protective relay systems because of design deficiencies or equipment problems.

- Breaker failure protection should be provided to trip all necessary local and remote breakers in the event that a breaker fails to clear a fault.  This protection need not be duplicated.

- On installations where freestanding or column-type current transformers are provided on one side of the breaker only, the protective relay system should be provided to detect a fault on the primaries of such current transformers.  This protection need not be duplicated.  Application of freestanding CTs requires extra care to ensure that the relaying is proper and that the schemes overlap.

Security

The protective relay system should be designed to isolate only the faulted element, except in those circumstances where additional elements should be tripped intentionally to preserve system integrity.  For faults external to the protected zone, each protective relay system should be designed to either not operate, or to operate selectively with other systems, including breaker failure.  (In this context, the limits of the protected zone are defined by the circuit breakers.)

Dependability and Security

- The protective relay system should be no more complex than required for any given application.

- To the maximum degree practicable, the components used in the protective relay system should be of proven quality, as demonstrated either by actual experience or by stringent tests under simulated operating conditions, to ensure that the reliability of the protective relay system is not degraded by the components.

- The protective relay system shall be designed to minimize the possibility of component failure or malfunction due to electrical transients and electromagnetic interference or external effects such as vibration, shock and temperature.

- Critical features associated with protective relay system and circuit breaker operation shall be annunciated or monitored.

- The protective relay system circuitry and physical arrangements shall be carefully designed so as to minimize the possibility of incorrect operations due to personnel error.

- Computerized fault studies shall be used during the planning or design stages to analyze the effects of an addition or modification to the ERCOT system and to determine proper protective relay system coordination.

Operating Time

The objective of the protective relay system is to take corrective action in the shortest practical time with due regard to selectivity, dependability and security. In cases where clearing times are deliberately extended, consideration should be given to the following:

- Effect on ERCOT System stability or reduction of stability margins.

- Possibility of causing or increasing damage to equipment and subsequent extended repair and/or outage time.

- Effect of disturbances on service to customers and neighboring Facility Owners.

Testing and Maintenance

- The design of the protective relay system both in terms of circuitry and physical arrangement shall facilitate periodic testing and maintenance.  Test devices or switches should be provided to eliminate the necessity for removing or disconnecting wires during periodic testing.

- Commissioning of new equipment should consist of the following steps:

- Relay installation wiring diagrams cross-checked against schematics

- After completion of construction, physical check of wiring and relay installation

- Check and testing before energizing of all equipment in the zone of protection, including relay testing.  It is desirable to test the relays at the setting the relay will have in service

- Check of supporting paperwork, such as relay test reports

- Check that relays physically agree with the relay settings

- Check that proper settings have been made

- Written record of trip check and energize procedure

- In-service measurement of voltage and current magnitudes and phase angles, and comparison to expected values and to other instrumentation

- Release to Facility Owner’s operating personnel for service

Analysis of System Performance and Associated Protection Systems

- Relay operation and settings shall be reviewed periodically and whenever significant changes in generating sources, transmission facilities, or operating conditions are anticipated.

- Naturally occurring faults and other system disturbances should be analyzed as a source of information as to the health of relay schemes in the System.  Sources of information usually available are:

- Short circuit study for the exact conditions of the fault

- Fault recorder traces

- Sequence of events data recording the opening and closing of contacts in the protective relay scheme and associated communication equipment

- Fault locator data

- SCADA (Supervisory Control And Data Acquisition) logger output of breaker operation and alarms

- Interviews with operating personnel and/or other witnesses

- Field report of relay flags and breaker counter changes

- Field report of the fault location, if found

- Records of relay setting, relay testing, trip check and energize procedures as carried out, in-service measurements, relay wiring diagrams and schematics, manufacturers' information

- Other coworkers and System Protection Task Force members

- Manufacturers' application and design engineers

- Steps one can follow in analyzing a disturbance are:

- Gather data

- Create a time line consisting of events and periods between events

- Compare actual and calculated values of current and voltage during the periods between events

- Compare actual and expected breaker operations and flags

- Choose the least complicated explanation for contradictory information and to fill in missing information

- Gather additional information as indicated to prove or disprove explanations

- Iterate

- Document by issuing a report of all findings, changes, and recommendations

- After a reasonable time, check back to see if the recommendations have been carried out

#### 7.3.5.2	Equipment and Design Considerations

Current Transformers

- Current transformers (CTs) associated with the protective relay system shall have adequate steady state and transient characteristics for their intended function.

- The output of each current transformer shall remain within acceptable limits for the connected burdens under all anticipated fault currents to ensure correct operation of the protective relay system.

- Current transformers or their secondary windings shall be located so that adjacent protection zones overlap.

- Current transformer secondary wiring shall be grounded at only one point. When multiple current transformers are interconnected, the combination shall have only one ground.

- Other considerations:

- Internal bushing CTs are preferred over external slip-over CTs

- 10L800 (C800) class CTs are preferred for relaying

- Breakers and free-standing CTs with four or more sets of CTs are preferred

- Over-the-bushing external CTs can sometimes solve problems when there aren't enough CTs.  Note that there may be an unprotected region between the external CT and the bushing CT.

- Shorting type terminal blocks should be provided for all CTs

Voltage Transformers and Potential Devices

- Voltage transformers (VTs) and potential devices associated with the protective relay system shall have adequate steady state and transient characteristics for their intended functions.

- Voltage transformers and potential devices shall have adequate volt-ampere capacity to supply the connected burden while maintaining their relay accuracy over their specified primary voltage range.

- Usually one set of VTs (with two separate secondary windings per VT) per bus (i.e. single bus substation configuration) or per power system element (i.e. ring bus and breaker-and-a-half substation configurations) is sufficient.  The two protective relay systems protecting ERCOT System facilities may use separate secondary windings of the VTs or one of the secondary windings may be dedicated to supplying the polarizing potential and the other winding used to supply other protection and monitoring functions.

- Voltage transformer and potential device secondary wiring shall be grounded at only one point.  (ANSI/IEEE C57 recommends grounding at the panel.)

- Voltage transformer installations shall be designed with due regard to ferroresonance due to capacitance across the interrupter at 138kV and above.

- Other considerations

- Special attention should be given to the physical properties of secondary circuit fuses

- Capacitor coupled voltage transformers are suitable for relaying and SCADA telemetry

- Report loss of VT voltage (VT fuse failure) over SCADA

Batteries and Direct Current (DC) Supply

- DC batteries associated with the protective relay system shall have a high degree of reliability.

- Two batteries each with its own charger should be provided at each location.  An acceptable alternative is one battery with two separately protected branches.  The systems protecting a zone shall be supplied from the separate sources or branches. For a new facility, two batteries shall be required in locations that remote backup clearing of lines and substation faults is not achieved. Where only one battery is used, remote backup clearing of line and substation faults is required.

- Each battery shall have sufficient capacity to permit operation of the station, in the event of a loss of its battery charger or the AC supply source, for the period of time necessary to transfer the load to the other battery or to re-establish the supply source. Each battery and its associated charger shall have sufficient capacity to supply its share of the DC load of the station.

- A fault at the battery terminals can only be interrupted by a mid-bank protective device.  If a mid-bank protective device is not used, then the connections between the battery terminals and the main protective devices shall possess the highest possible degree of reliability.

- The battery chargers and all associated circuits shall be protected against short circuits.  All protective devices shall be coordinated to minimize the number of DC circuits interrupted.

- The regulation of DC voltage shall be designed such that, under all possible loading conditions, voltage within acceptable limits will be supplied to all devices.

- DC systems shall be monitored to detect abnormal voltage levels, both high and low, DC grounds, and loss of AC to the battery chargers.  Loss of DC to relay schemes shall be alarmed.  Also, where possible the loss of AC to the battery chargers and loss of DC should be provided as SCADA alarm inputs.

- DC systems shall be designed to minimize AC ripple and voltage transients.

- The DC circuit protective devices used shall have published DC interrupting ratings suitable for the required circuit duty.

AC Auxiliary Power

- There should be two sources of station service AC supply, each capable of carrying all the critical loads associated with the protective relay system.

- Failure of station service AC supply should be alarmed over SCADA.

Circuit Breakers

- Two trip coils, one associated with each protection system, shall be provided for each operating mechanism.  The failure of one coil shall not damage or impair the operation of the other coil.

- The design shall be such that the breaker will operate if either both trip coils are energized simultaneously, or either trip coil alone, and verified by tests.

- Circuit breaker auxiliary switches used in protection systems should be highly reliable with a positive make-break action and good contact wipe.  Multiplier contacts simulating breaker auxiliary switches should be used with caution in protection systems.

- A three-phase and line-to-ground interrupting study to validate or indicate breaker interrupting rating shall be performed.

Communications Channels

- Where communication channels are required for the protective relay system purposes, the communication facilities shall have a degree of reliability no less than that of the other protective relay system components.  For extra security, the output contacts from two independent channels may be wired in series.

- Where communication channels are required in each of the two protective relay systems, the channels shall be separated physically and designed to minimize the risk of both channels being disabled simultaneously by a single contingency.

- Communication channels shall be provided with means to verify signal performance.

- Other considerations

- Report loss of channel over SCADA

- Automatic testing of power line carrier (PLC) is desirable to reduce false trips from failure to block

- Split up PLC loads between DC sources so that loss of one fuse does not disable all the carrier sets.  If all the carrier sets were to be disabled, then multiple false trips during a fault could result.

Control Cables and Wiring

- Control cables, wiring and auxiliary control devices should be such as to assure high reliability with due consideration to published codes and standards, fire hazards, current-carrying capacity, voltage drop, insulation level, mechanical strength, routing, shielding, grounding and environment.

- Other considerations

- Shielded cable may be necessary for certain relay and SCADA applications

- AC or DC go-and-return functions should be implemented in the same cable to avoid induction loops

- Individual wires in cables should have colored jackets, not black jackets with a "color" printed on the jacket

- Standardization of the relationship between wire colors and functions is desirable

- No splice in any wire or cable

- All cables terminated on terminal blocks

Environment

- Means shall be employed to maintain environmental conditions that are favorable to the correct performance of the protective relay system.  Particular attention should be given to solid-state equipment installations.

- Other environmental hazards to look out for:

| - Fire ants | - Rats |
| --- | --- |
| - Snakes | - Dust, dirt, grime |
| - Trash and leftover hardware | - Water |
| - Gunfire | - Theft of substation and transmission grounds |
| - Hand-held radio keyed near solid-state relays | - Batteries located in same room as relays (battery fires) |
| - Severe cold weather conditions can impact operation of circuit breakers, DC battery, and carrier signals. |  |

#### 7.3.5.3	Specific Application Considerations

Transmission Line Protection

- Each of the two independent protective relay systems shall detect and initiate action to clear any line fault without undue system disturbance.  The protective relay system shall operate for line faults so that, if ultimate clearing should be accomplished by a breaker failure scheme, a widespread disturbance will not result.  A protective relay system, which can operate for faults beyond the zone it is designed to protect, shall be selective in time with other protective relay system, including breaker failure.

- Transmission line protection should consist of:

- Primary phase and ground protection over a communications channel.

- Backup relaying with at least two zones of phase protection.

- Backup relaying with at least two zones of ground protection, or backup relaying with ground directional overcurrent relaying (time delay and instantaneous).

- "Ground chain protection" to recognize and trip for a three-phase fault right at the terminals, in service for a short period of time just as the line is energized, for lines with line side VTs.

- Recognition and trip for open conductor is desirable but not required.

- Overload protection is provided by SCADA analog alarms and dispatcher discretion.

- Fault detector relays to supervise phase distance relaying to prevent inadvertent trip due to VT failure.

- Short lines may require special attention, such as dual primary schemes, etc.

- Fuses shall not be used in the 3Vo polarizing supply for ground relays.

- The setting for synchronization check relays should be based on system studies that identify the voltage angles necessary for a successful re-close.

Transmission Station Protection

- Each zone in a station shall be protected by two independent protective relay systems.  For zones not protected by line protection, at least one of the two protective relay systems shall be a differential type.

- The protective relay system shall be designed to operate for station faults so that, if ultimate clearing is accomplished by a breaker failure scheme, a widespread disturbance will not result.  The protective relay system shall be designed to operate properly for the anticipated range of currents.

- Station protection should consist of:

- Bus differential or bus overcurrent protection of all buses

- All transformers protected by transformer differential, transformer overcurrent, or fuses (for small transformers).  Note that ferroresonance is possible for fused transformers above 69kV.

- Sudden pressure relay protection for transformer main tanks and transformer tap changer compartments

Breaker Failure Protection

- Breaker failure protection should be provided to trip all necessary local and remote breakers in the event that a breaker fails to clear a fault.

- The breaker failure protection should be initiated by each of the protection systems that trip that breaker.  It is not necessary to duplicate the breaker failure protection itself.

- Induction cup or solid state fault current detectors shall be used to determine if a breaker has failed to interrupt.

- Plunger or clapper type overcurrent relays are not recommended as breaker failure fault detectors.

Generator Protection

- Generator faults shall be detected by more than one protective relay system.  These may include faults in the generator or generator leads, unit transformer, and unit-connected station service transformer.

- Generators shall be protected to keep damage to the equipment and subsequent outage time to a minimum.  In view of the special consideration of generator unit protection, the following are some of the conditions that should be detected by the protection systems:

- Unbalanced phase currents

- Loss of excitation

- Over-excitation

- Field ground

- Inadvertent energization (reverse power)

- Uncleared system faults

- Off-frequency

It is recognized that the overall protection of a generator will also involve non-electrical considerations.  These have not been included as part of this criteria.

- The apparatus shall be protected when the generator is starting up or shutting down as well as running at normal speed; this may require additional relays, as the normal relays may not function satisfactorily at low frequencies.

- A generator shall not be tripped for a system swing condition except when that particular generator is out of step with the remainder of the system.  This does not apply to protective relay system designed to trip the generator as part of an overall plan to maintain stability of the ERCOT System.

- The loss of excitation relay shall be set with due regard to the performance of the excitation system.

Automatic Under-frequency Load Shedding Protection Systems

- Automatic under-frequency load shedding systems are classified as protective relay systems.  The maintenance requirements, discussed in Section B.3.4 of this Appendix, apply to under-frequency load shedding protection systems as well.

- Automatic under-frequency load shedding systems are generally located on equipment operated below 60 kV; however, they have a direct effect on the operation of the System during major emergencies.

- The criteria for the operation of these protection systems are detailed in Operating Guide 3  - Application of Under-frequency Relaying

- Automatic under-frequency load shedding protection systems need not be duplicated.

- Generator and turbine under-frequency protection systems where applicable shall be coordinated with Operating Guide No. I.F. - Application of Under-frequency Relaying.  If the generator and turbine under-frequency protection systems cannot be coordinated with Operating Guide 3 – System Operations, this shall be reported by the Facility Owner to ERCOT and reviewed by the ERCOT Reliability and Security Subcommittee.

- On pressurized water reactor steam supply units where under-frequency related protection systems are installed to detect loss of coolant flow condition, these protection systems shall be coordinated with the automatic under-frequency load shedding program.

- Automatic load restoration for a UFLS operation is not currently utilized in ERCOT.

Automatic Under-Voltage Load Shedding Protection Systems

Automatic under-voltage load shedding systems are classified as protective relay systems. The maintenance requirements, discussed in Section B.3.4 of this Appendix, apply to under-voltage load shedding protection systems as well.

- The requirement for under-voltage relaying shall be determined by system studies performed / administered by ERCOT designated working groups or equipment owners. The system studies should indicate the following:

- Amount of load to be shed to restore voltage to minimum acceptable level or higher,

- The minimum and maximum time delay allowed before automatically shedding load,

- The voltage level(s) at which to initiate automatic relay operation.

- The location(s) for effectively applying under-voltage load shedding protection systems.

- Automatic under-voltage load shedding protection systems need not be duplicated.

- Generator under-voltage protection systems, where applicable, shall be coordinated with automatic under-voltage load shedding.  If the generator under-voltage protection systems cannot be coordinated with automatic under-voltage load shedding, this should be reported to and reviewed by the ERCOT designated working groups or equipment owners performing the system study of item (1) above.

- Under-voltage protection systems shall be coordinated with all other voltage sensitive protective devices and control schemes.

- Automatic load restoration for a UVLS operation is not currently utilized in ERCOT.

7.4	Document Control

Authorities

| Prepared by | Date Completed | Reviewed by | Date Authorized |
| --- | --- | --- | --- |
| B. Brodie, Technical Writer | 12/07/2000 | B. Garza, Chair Joint Operating Guides WG |  |
| Isabel Flores | 04/16/2002 | OGRTF/ROS |  |
| I. Flores | 06/25/2002 | OGRTF/ROS |  |
| I Flores | 08/20/2002 | OGRTF/RPS | July 11, 2002 |
| I. Flores | 12/01/2002 | OGRTF | October 24, 2002 |
| I. Flores | 01/01/2003 | OGRTF | January 1, 2003 |
| I. Flores | 03/01/2003 | OGRTF |  |

Distribution List

| Name | Organization |
| --- | --- |
| Operating Guide Revisions Task Force | ERCOT |
| Operations | ERCOT |
| Technical Advisory Committee | ERCOT |
| Reliability Operations Subcommittee | Technical Advisory Committee |

Change History

| Issue | Reason for issue | Date |
| --- | --- | --- |
| Version 0.1 | Draft for Review | December 7, 2000 |
| Version 0.2 | Insert comments | December 29, 2000 |
| Version 0.3 | Insert comments from seminar | January 19, 2001 |
| Version 0.4 | Comments from second Working Group | February 5, 2001 |
| Version 1.0 | Updated from Working Group comments. Submitted to Technical Advisory Committee to approve handover to the Reliability Operating Subcommittee | February 28, 2001 |
| May 1, 2002 | OGRR103 | May 1, 2002 |
| July 1, 2002 | OGRR104 | July 1, 2002 |
| September 1, 2002 | OGRR107 & OGRR109 | September 1, 2002 |
| December 1, 2002 | Reformatted numbering from Appendix B to Section 7. | December 1, 2002 |
| January 1, 2003 | OGRR121 revised Section 7.2.2.5 for fault recording equipment. | January 1, 2003 |
| March 1, 2003 | Formatted header and page numbering. | March 1, 2003 |