ERCOT Staff Investigation of Voltage Problems and Recommended Solutions

in the ERCOT Western Region

March 2003

Executive Summary

Recurring high voltages in West Texas has justified keeping several generation units reliability must run status.  ERCOT Staff investigated this issue and has determined that a minimum installation of 200 Mvar of additional reactors at various locations will relieve the situation.  Operations personnel indicate that tuning of autotransformer taps has not been successful at relieving the high voltages.  Better control of load power factor during light load conditions also has a significant impact on the high voltages.

Input was received from the initial study and it was expanded to investigate the voltage problem with reactive capability modeled (0.98 & 0.95) at the renewable generation sites.  This additional study indicates that with this additional reactive capability, the high voltage problem on the 345 kV system remained and additional reactors are still necessary.  Many of local voltages were improved around the renewable generation sites.  The highest voltages were indicated in the Abilene, San Angelo and Sweetwater areas of West Texas.

ERCOT Staff along with the West Regional Planning Group is moving forward to install at least 200 Mvar of additional reactors at Twin Buttes, Red Creek, Mulberry Creek, Morgan Creek, Odessa and Moss.  The highest need for reactors is in the Abilene and San Angelo areas.

Introduction and Background

The ERCOT system operators are experiencing a recurring high-voltage problem in the Western Region during light load conditions.  The operating procedure to control voltages is based on system load and requires the dispatch of Rio Pecos 6, San Angelo 2, and Fort Phantom 2 in different combinations, minimum generation levels.

The owner of these generating facilities would like to mothball them because they are not profitable in the market.

High voltages are unacceptable on the transmission system because they can cause equipment failure, they can endanger people, and they can cause mis-operation of impedance relays.

The voltage control problem the operators experience is not apparent in the standard ERCOT SSWG 2003 data set A base cases.

Purposes

The primary purpose of this study is to find reasonable solutions to the voltage problems that do not involve RMR generation.

The secondary purpose of the study is to determine which lines can be switched out of service to reduce voltage immediately before the recommended alternative can be constructed, and to review this with the system operators.

Scope of the Investigation

The following basic questions must be answered before alternatives to RMR generation can be identified:

- What are the reactive resources and how are they operated?

- Are these correctly modeled in the SSWG base cases?

- What is typical reactive loading in the Western Region during light load conditions?

- Is this accurately reflected in the SSWG base cases?

The time frame of interest is 2003, especially during spring and fall when the system load is lowest.  The study area includes Oklaunion, Bowman, Parker, Comanche Peak, Comanche SS, Menard, Sonora, and all of the ERCOT system west of these substations.  Fort Worth, Waco, Austin, San Antonio, Laredo, and all points east of these cities are not included.

Methodology

Once the basic research is complete, 2003 spring and fall off-peak study cases can be developed.  There will be at least one study case with minimal generation and others with wind power generation at varying levels.

Findings

1.  Table 1 Summary of reactive resources in the Western Region:

| Reactive Resources in the Western Region |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Passive - Line Charging MVA (capacitive) |  |  | (03summer base case data) |  |  |
| Oncor 345kV | 12.20085 |  |  |  |  |
| Oncor 138kV | 2.63682 |  |  |  |  |
| AEP 345kV | 5.02445 |  |  |  |  |
| AEP 138kV | 1.93981 |  |  |  |  |
| Total | 21.80193 | p.u. @ 100 MVA |  |  |  |
|  | 2180.2 | MVA |  |  |  |
| Remotely Switchable Capacitor Banks |  |  | (state estimator data, corrected) |  |  |
| Oncor | 454.0 |  |  |  |  |
| AEP | 284.5 |  |  |  |  |
| Total | 738.5 | MVA |  |  |  |
| Remotely Switchable Reactor Banks |  |  | (state estimator data, corrected) |  |  |
| Oncor | -595.0 |  |  |  |  |
| AEP | -223.0 |  |  |  |  |
| Total | -818.0 | MVA |  |  |  |
| Generator Capacitve Limits | Qmax |  | (03fall off-peak base case data) |  |  |
| TXU Energy | 2535 |  |  |  |  |
| AEP | 865 |  |  |  |  |
| Totals | 3382 |  |  |  |  |
| Generator Reactive Limits | Qmin |  | (03fall off-peak base case data) |  |  |
| TXU Energy | -1158 |  |  |  |  |
| AEP | -479 |  |  |  |  |
| Totals | -1619 |  |  |  |  |

The complete lists of the reactive resources are in Appendices A – H at the end of the report.  The reactive resources modeled in the planning base cases mostly agree with those modeled in the operating model.  A few corrections will be given to SSWG for the base cases and to the operations department for the state estimator.

2.  The importance of load power factor:

The power factor of the loads modeled in the western region in the System Planning base cases is significantly different from the power factor of the loads measured by SCADA and/or calculated by the state estimator.  The bus voltages in the area vary as the load power factor is adjusted in the model.  Unfortunately the SCADA system is only capturing about one-third of the load data in the area of interest.  The other two-thirds are considered “suspect,” not necessarily wrong but not known to be right.

Table 2 Summary of reactive load modeled in the ERCOT spring and fall off-peak cases:

PTI INTERACTIVE POWER SYSTEM SIMULATOR--PSS/E      MON, FEB 17 2003  13:23

SS03SPG2 - 2003 SPRING OFF-PEAK BASE CASE - ERCOT ROS SSWG          AREA TOTALS

UPDATED 1/27/03 - ERCOT SPRING OFF-PEAK, WIND 20% NAMEPLATE          IN MW/MVAR

FROM      TO    TO BUS  TO LINE     FROM      TO            DESIRED

AREA  GENERATION     LOAD    SHUNT    SHUNT CHARGING  NET INT   LOSSES  NET INT

1      10270.4  11384.1      0.0      0.0      0.0  -1400.2    286.5      0.0

ONCORTSP  2294.1   3123.7    395.1      0.0   4893.6   -126.1   3794.9

8       2695.9   2941.9      0.0      0.0      0.0   -319.1     71.9      0.0

AEP TSP     16.4    584.1    201.1      0.0   1500.2    113.9    617.1

TOTALS   12966.4  14326.1      0.0      0.0      0.0  -1719.3    358.4      0.0

2310.5   3707.8    596.2      0.0   6393.8    -12.3   4412.1

PTI INTERACTIVE POWER SYSTEM SIMULATOR--PSS/E      MON, FEB 17 2003  13:29

SS03FAL2 - 2003 FALL OFF-PEAK BASE CASE - ERCOT ROS SSWG            AREA TOTALS

UPDATED 1/27/03 - ERCOT   FALL_OFF_BASE, WIND 20% NAMEPLATE          IN MW/MVAR

FROM      TO    TO BUS  TO LINE     FROM      TO            DESIRED

AREA  GENERATION     LOAD    SHUNT    SHUNT CHARGING  NET INT   LOSSES  NET INT

1       9645.2  10626.7      0.0      0.0      0.0  -1223.2    241.8      0.0

ONCORTSP  1340.4   2925.9    324.6      0.0   5184.9     15.6   3259.1

8       2828.0   2818.2      0.0      0.0      0.0    -58.8     67.3      0.0

AEP TSP     11.5    558.1    262.2      0.0   1531.5    132.1    590.1

TOTALS   12473.2  13444.9      0.0      0.0      0.0  -1282.0    309.1      0.0

1351.9   3484.0    586.8      0.0   6716.4    147.8   3849.3

Note that the Oncor load power factor is 0.964 for each season and the AEP load power factor for each season is 0.981.

Table 3 Summary of reactive load modeled by the state estimator for January 9, 2003, 9:15 AM (similar total system load level):

FROM      TO    TO BUS  TO LINE     FROM      TO

ZONE  GENERATION     LOAD    SHUNT    SHUNT CHARGING  NET INT   LOSSES

1       9680.1  10315.0      0.0      0.0      0.0   -929.9    295.0

TUE TU_E  1090.7   1820.2   -142.5      0.0   3974.0   -669.5   4056.5

2        872.0    973.9      0.0      0.0      0.0   -126.7     24.8

TUE TU_W  -197.6    128.1    184.8      0.0    893.4    213.4    169.5

7       1149.8    726.9      0.0      0.0      0.0    385.0     37.8

CSW WTU     79.9    135.2     85.8      0.0    556.3    137.9    277.4

8          0.0     62.6      0.0      0.0      0.0    -62.7      0.1

CSW RAYB     0.0     21.6      0.0      0.0      5.7    -16.0      0.2

9       1489.8   1759.2      0.0      0.0      0.0   -322.2     52.7

CSW CBEN   260.4    351.5   -104.0      0.0    559.6    161.7    410.9

TOTALS   13191.6  13837.7      0.0      0.0      0.0  -1056.5    410.5

1233.4   2456.6     24.0      0.0   5989.1   -172.6   4914.5

Note that the overall Oncor load power factor is 0.985, and the CSW WTU load power factor is 0.983.

3.  The importance of windpower:

There are 14 windpower plants in the area with a total capability of 1007 MW.  (Eleven of these plants cannot provide or absorb any reactive power.)  The transmission system will not be upgraded enough to deliver this power to other loads for several years.  Until then some of the generator owners are being allowed to operate beyond the FCITC limit with the risk of being tripped out of service for any transmission disturbance.  In the spring off-peak case it is possible to dispatch 60% of the windpower without transmission overloads.  In the fall off-peak case it is possible to dispatch up to 80% of the windpower without transmission overloads.

The generation dispatch of the 2003 Fall off-peak base case is shown in Appendix I with the windpower generators in blue.

The bus voltages have been reviewed at load power factors from 0.964 to 0.990, and windpower levels of 200 MW to 800 MW.

Results

Only the voltages that exceeded 105% nominal for at least one condition were recorded.  In the spring off-peak case with Morgan Creek 6 dispatched at 250 MW there were no overvoltages at any bus in the western area for any level of load power factor or windpower.

In the fall off-peak case (Morgan Creek 6 not dispatched) there are ten 345kV, twelve 138kV, and four 69kV busses showing high voltage for at least one condition.  The data is attached in Appendix J with high voltages in red.

(The high voltage at Live Oak 138kV is obviously due to a 12 Mvar capbank at the 69kV bus.  According to the AEP system operator this capbank is SCADA controlled and he keeps it out of service during light load conditions.  SSWG will be informed so the base cases can be revised.)

Recommended Solutions

Permanent:

Install reactor banks and controls at the 345kV busses with the worst overvoltages.  They should automatically switch themselves in and out to maintain local bus voltage from 0.95 to 1.05 per unit.  The following set is one possible arrangement that works for windpower dispatch from 200 MW to 800 MW and load power factor up to 0.990:

- 75 Mvar reactor bank at Twin Buttes 345

- 75 Mvar reactor bank at Sweetwater 345

- 45 Mvar reactor bank at Odessa 345

A different set that works for the same range of operating conditions:

- 75 Mvar reactor bank at Twin Buttes 345

- 45 Mvar reactor bank at Sweetwater 345

- 45 Mvar reactor bank at Odessa 345

- 45 Mvar reactor bank at Mulberry 345

All major new transmission lines must be built with reactive compensation as well.

Interim:

Until the reactors are installed, the system operators can correct or relieve some overvoltages by tripping one of the Odessa – Morgan Creek 345kV lines out of service.  Each of these lines is responsible for a little more than 80 Mvar of line charging.  Of course the system is less secure with a large circuit tripped, so this is not ideal even when it works.

Depending on the load power factor and windpower generation level, this may not be enough to relieve all overvoltages.  The next step is to dispatch a local generator with good reactive capability.  Oklaunion, Graham, and Comanche Peak are not local enough.  Morgan Creek 6 and TIE are local enough and each has good reactive capability.

Corrections and Comments from the Western Regional Planning Group

- The two Indian Mesa windpower plants are modeled in the base cases as if they have no reactive capability.  According to Rick Walker these plants are capable of operating at approximately 99% lagging or 86% leading.  This information has been sent to SSWG to correct the base cases.

- AEP agrees with installing reactive compensation on new 345kV lines in the area.

- AEP planners have suggested that the model could be “tuned” to get better voltages by manipulating the LTC taps.  True.  The AEP operator was asked if he could likewise manipulate the LTCs from his control desk to achieve the same thing.  According to him the LTC automatic controls do not produce the best results at very light load and the operators intervene as necessary.  Does the operator ever reach the LTC limits before the voltages are in the acceptable range?  Yes, at lightest load.

- LCRA wanted to know if the proposed reactor banks would be connected to the autotransformer tertiaries.  That decision belongs to the TSPs.

- TNMP suggested installing controls on distribution capacitor banks so the operators can lower the load power factor when needed as a less expensive alternative.  This is a good idea that should be evaluated by the TSPs for each proposed reactor bank.

- TNMP has not observed high voltages but also doesn’t have SCADA on much transmission.

- Oncor recommends that future wind plants should be installed with adequate dynamic reactive control to prevent worse problems later.

- Oncor recommends verifying the light load power factor and examining opportunities for adjusting capacitor controls on distribution capbanks.

- Oncor would prefer to install any needed reactors on the tertiary of 345/138 kV autotransformers where possible, rather than the 345 kV system.  Available tertiary capacity exists at Morgan Creek, Odessa EHV and Moss.

Reactors that are in the Plans but not in the 2003 Off-Peak Cases

- 36 Mvars for the Twin Buttes autotransformer tertiary, March 2004, per Tom Bao, LCRA and 2006 minimum case.

Addendum:  What if the Windpower Generators Had Reactive Capability Like Other Generators?

The study was repeated with the generator models of the windpower stations changed as if the turbines did have reactive capability.  The levels studied were 98% power factor of dispatched power and 95% power factor of dispatched power.  The windpower generators that are already modeled with reactive capability were not changed in the cases.

Conventional large generators are modeled with full reactive capability available at any dispatch power level.  This practice was not applied here, so the study is considering “fewer turbines at full power each” rather than “all turbines, each at less than full power.”

For either 98% or 95% power factor reactive support, all of the voltage problems seen on the 138kV and 69kV systems were fixed.  Nine 345kV busses still experienced voltages above 1.05 per unit for some load power factors and some windpower generation levels.

For the sake of comparison, the transmission reactors that would be recommended if all the existing windpower generators could provide reactive support at 98% or 95% power factor of dispatched power are:

- 60 Mvar at Twin Buttes 345kV or autotransformer tertiaries

- 60 Mvar at Sweetwater 345kV

- 24 Mvar at EnronIPP 345kV

While the voltages were generally better for the 95% reactive support level, the same set of transmission reactors were required to fix the remaining problems for either 95% or 98% reactive support from existing wind turbines.

The tables of voltages for this addendum to the study are in Appendices K and L.

Appendices	Page

Appendix A Oncor 345kV Line Charging	9

Appendix B Oncor 138kV Line Charging	10

Appendix C AEP 345kV Line Charging	16

Appendix D AEP 138kV Line Charging	17

Appendix E Oncor Switchable Capacitor and Reactor Banks	20

Appendix F AEP Switchable Capacitor and Reactor Banks	22

Appendix G Oncor Generator Reactive Limits	23

Appendix H AEP Generator Reactive Limits	24

Appendix I 2003 Fall Off-Peak Base Case Generation Dispatch	25

Appendix J Fall Off-Peak Voltages for Varying Windpower

and Oncor Load Power-Factors	27

Appendix K  Fall Off-Peak Voltages for Varying Windpower and Oncor

Load Power-Factors if the Existing Windpower Generators

Provided Reactive Support, 98% Power Factor	31

Appendix L  Fall Off-Peak Voltages for Varying Windpower and Oncor

Load Power-Factors if the Existing Windpower Generators

Provided Reactive Support, 95% Power Factor	35

Appendix A Oncor 345kV Line Charging

| X------FROM------X X-------TO-------X Z S |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| BUS# | NAME | BUS# | NAME | LINE R | LINE X | CHRGING | RATEA | RATEB | RATEC | LENGTH |
| 1018 | MOSS | 1022 | MIDLND E | 0.00227 | 0.01968 | 0.37116 | 1052 | 1052 | 1072 | 41.4 |
| 1018 | MOSS | 1026 | ODES EHV | 0.00082 | 0.00714 | 0.13361 | 1052 | 1052 | 1072 | 15 |
| 1020 | EHV TIET | 1026 | ODES EHV | 0 | 0.0001 | 0 | 1195 | 1195 | 1195 | 0 |
| 1020 | EHV TIET | 1029 | ODEHV 2T | 0 | 0.0001 | 0 | 1195 | 1195 | 1195 | 0 |
| 1021 | MIDL E T | 1022 | MIDLND E | 0 | 0.0001 | 0 | 717 | 717 | 1072 | 0 |
| 1021 | MIDL E T | 1025 | FS COGEN | 0.00268 | 0.02458 | 0.41006 | 896 | 896 | 1072 | 48.4 |
| 1025 | FS COGEN | 1030 | MRGN CRK | 0.002 | 0.01833 | 0.30788 | 717 | 717 | 1072 | 36.2 |
| 1026 | ODES EHV | 1028 | ODEHV 1T | 0 | 0.0001 | 0 | 526 | 526 | 1072 | 0 |
| 1028 | ODEHV 1T | 1030 | MRGN CRK | 0.005 | 0.04346 | 0.81588 | 526 | 526 | 1072 | 91.2 |
| 1029 | ODEHV 2T | 1030 | MRGN CRK | 0.005 | 0.04346 | 0.81588 | 526 | 526 | 1072 | 91.2 |
| 1030 | MRGN CRK | 1050 | ENRONIPP | 0.00179 | 0.01556 | 0.2922 | 717 | 717 | 1072 | 32.7 |
| 1030 | MRGN CRK | 1420 | SWEETWTR | 0.00206 | 0.01787 | 0.33556 | 717 | 717 | 1072 | 37.5 |
| 1030 | MRGN CRK | 1430 | GRAHAM | 0.00856 | 0.07935 | 1.31229 | 717 | 717 | 1072 | 153 |
| 1030 | MRGN CRK | 6009 | TWBT7 | 0.0021 | 0.03619 | 0.66499 | 1515 | 1770 | 1515 | 75 |
| 1050 | ENRONIPP | 6235 | ABMULCW7 | 0.00179 | 0.01556 | 0.2922 | 717 | 717 | 1072 | 32.7 |
| 1420 | SWEETWTR | 1430 | GRAHAM | 0.00653 | 0.05679 | 1.06615 | 717 | 717 | 1072 | 119.2 |
| 1422 | BOWMAN | 1425 | FISHRDSS | 0.00083 | 0.00719 | 0.13459 | 717 | 717 | 1072 | 15.1 |
| 1422 | BOWMAN | 1429 | JXBRO SS | 0.00255 | 0.02355 | 0.3852 | 1072 | 1072 | 1072 | 45.9 |
| 1422 | BOWMAN | 1430 | GRAHAM | 0.00254 | 0.02191 | 0.41797 | 717 | 717 | 717 | 46.4 |
| 1425 | FISHRDSS | 6100 | OKLAEHV7 | 0.00291 | 0.02641 | 0.43348 | 717 | 717 | 1072 | 52 |
| 1429 | JXBRO SS | 1430 | GRAHAM | 0.00103 | 0.01412 | 0.3745 | 1631 | 1631 | 1631 | 35 |
| 1430 | GRAHAM | 1436 | PARKER | 0.00334 | 0.02902 | 0.54479 | 1052 | 1052 | 1072 | 60.9 |
| 1430 | GRAHAM | 1873 | BENBRK | 0.00434 | 0.03758 | 0.70717 | 789 | 789 | 1072 | 78.9 |
| 1430 | GRAHAM | 6230 | ABMULCE7 | 0.00459 | 0.03987 | 0.74847 | 717 | 717 | 1072 | 83.7 |
| 1440 | CMCHE SS | 1900 | COM PEAK | 0.00311 | 0.02489 | 0.55266 | 956 | 956 | 1072 | 56.5 |
| 1440 | CMCHE SS | 6444 | SAREDCK7 | 0.00338 | 0.05793 | 1.08416 | 1515 | 1770 | 1515 | 121.3 |
|  |  |  |  |  |  | 12.20085 |  |  |  |  |

Appendix B Oncor 138kV Line Charging

| X------FROM------X X-------TO-------X Z S |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| BUS# | NAME | BUS# | NAME | LINE R | LINE X | CHRGING | RATEA | RATEB | RATEC | LENGTH |
| 275 | LNPLNTRD | 1624 | LEON | 0 | 0.0001 | 0 | 0 | 0 | 0 | 0 |
| 276 | HGHWY101 | 1619 | COLNY CK | 0 | 0.0001 | 0 | 0 | 0 | 0 | 0 |
| 282 | EOLIANRD | 1614 | BRECK | 0 | 0.0001 | 0 | 0 | 0 | 0 | 0 |
| 283 | ZEPHYR | 1654 | ZEPHYR M | 0 | 0.0001 | 0 | 0 | 0 | 0 | 0 |
| 290 | SHILOH | 1651 | CMCHE | 0 | 0.0001 | 0 | 0 | 0 | 0 | 0 |
| 292 | HOLDER | 1655 | BRNWD SS | 0.0218 | 0.0772 | 0.0193 | 128 | 171 | 171 | 18.6 |
| 296 | STPHVLTP | 1641 | STPHVIL | 0.00101 | 0.00586 | 0.00164 | 214 | 214 | 214 | 1.5 |
| 300 | JOHNSVIL | 1645 | JOHNVL M | 0 | 0.0001 | 0 | 0 | 0 | 0 | 0 |
| 301 | LINGLEVL | 1640 | LNGLVL M | 0 | 0.0001 | 0 | 0 | 0 | 0 | 0 |
| 302 | SELDEN | 1644 | SELDEN M | 0 | 0.0001 | 0 | 0 | 0 | 0 | 0 |
| 322 | LIPAN | 1595 | LIPAN | 0 | 0.0001 | 0 | 0 | 0 | 0 | 0 |
| 331 | MILLER | 1578 | PALOPT M | 0.0029 | 0.0271 | 0.0089 | 359 | 359 | 359 | 7.7 |
| 340 | WSTWTHFD | 1580 | MINWL 1 | 0.00837 | 0.04783 | 0.01359 | 214 | 214 | 214 | 12.3 |
| 511 | AGNESSW | 1592 | WTHFRD | 0.00006 | 0.0005 | 0.00007 | 180 | 180 | 180 | 0.1 |
| 520 | ALEDOTP | 1579 | ALEDO TU | 0 | 0.0001 | 0 | 0 | 0 | 0 | 0 |
| 618 | LONESTAR | 1561 | ALVORD | 0 | 0.0001 | 0 | 0 | 0 | 0 | 0 |
| 622 | BOWIE | 1469 | SUNSET | 0.0093 | 0.0328 | 0.0082 | 128 | 171 | 171 | 8 |
| 631 | NEWPORT | 1470 | NEWPRT M | 0 | 0.0001 | 0 | 0 | 0 | 0 | 0 |
| 721 | WICHSUTH | 1498 | WF COGEN | 0 | 0.0001 | 0 | 200 | 200 | 200 | 0 |
| 743 | SALTCK4 | 1064 | SUN | 0.02387 | 0.13767 | 0.03736 | 175 | 236 | 236 | 36 |
| 770 | AROWHEAD | 1478 | AROHD M | 0 | 0.0001 | 0 | 0 | 0 | 0 | 0 |
| 773 | SCOTLAND | 1474 | SCOTLD M | 0.0018 | 0.0059 | 0.00158 | 126 | 171 | 171 | 1.5 |
| 787 | OLNEY | 1477 | RICE | 0.02 | 0.0709 | 0.01772 | 72 | 72 | 171 | 17.1 |
| 792 | MURRAY | 1371 | MURRAY M | 0 | 0.0001 | 0 | 0 | 0 | 0 | 0 |
| 794 | JACKSBRO | 1601 | GRAHAM E | 0 | 0.0001 | 0 | 0 | 0 | 0 | 0 |
| 797 | MARKLEY | 1476 | MARKLEY | 0 | 0.0001 | 0 | 0 | 0 | 0 | 0 |
| 1010 | PERMIANB | 1019 | MOSS | 0.02397 | 0.13886 | 0.03852 | 191 | 191 | 214 | 35.2 |
| 1010 | PERMIANB | 1074 | WINK SS | 0.01409 | 0.06659 | 0.01759 | 143 | 143 | 186 | 16.5 |
| 1010 | PERMIANB | 1087 | WRDGLF T | 0.0003 | 0.00107 | 0.00055 | 239 | 239 | 248 | 0.4 |
| 1010 | PERMIANB | 1105 | MONAH 1T | 0.00001 | 0.0005 | 0.00001 | 186 | 186 | 186 | 0 |
| 1010 | PERMIANB | 1107 | MONAH 2T | 0.00269 | 0.01561 | 0.00433 | 210 | 210 | 214 | 4 |
| 1010 | PERMIANB | 1145 | AM GLDSM | 0.02879 | 0.13537 | 0.0362 | 186 | 186 | 186 | 33.7 |
| 1010 | PERMIANB | 1292 | ECTR HRP | 0.02068 | 0.11989 | 0.03321 | 210 | 210 | 214 | 30.4 |
| 1010 | PERMIANB | 6655 | BARRILA4 | 0.05933 | 0.2131 | 0.05479 | 147 | 155 | 147 | 52.2 |
| 1019 | MOSS | 1113 | ODESA SW | 0.00471 | 0.02676 | 0.00765 | 143 | 143 | 214 | 6.9 |
| 1019 | MOSS | 1129 | WESTOVER | 0.00232 | 0.01371 | 0.00371 | 210 | 210 | 211 | 3.4 |
| 1019 | MOSS | 1143 | AMOCNC T | 0.01102 | 0.05232 | 0.01371 | 143 | 143 | 186 | 12.9 |
| 1019 | MOSS | 1176 | GRANDVW | 0.01817 | 0.10316 | 0.02964 | 214 | 214 | 214 | 26.6 |
| 1019 | MOSS | 1180 | ECTR HIL | 0.00807 | 0.04586 | 0.01315 | 210 | 210 | 214 | 11.8 |
| 1019 | MOSS | 1292 | ECTR HRP | 0.00152 | 0.00879 | 0.00244 | 191 | 191 | 214 | 2.2 |
| 1023 | MIDLND E | 1116 | WINDWOOD | 0.00168 | 0.00716 | 0.00181 | 143 | 143 | 162 | 1.7 |
| 1023 | MIDLND E | 1132 | MIDL DWN | 0.0029 | 0.01336 | 0.00373 | 143 | 143 | 186 | 3.4 |
| 1023 | MIDLND E | 1178 | ADOBE MD | 0.00204 | 0.01162 | 0.00333 | 214 | 214 | 214 | 3 |
| 1023 | MIDLND E | 1184 | GODDARD | 0.00615 | 0.03493 | 0.01001 | 214 | 214 | 214 | 9 |
| 1023 | MIDLND E | 1324 | BIG SPGW | 0.11578 | 0.18379 | 0.03631 | 84 | 84 | 84 | 37.2 |
| 1024 | FS COGEN | 1332 | COSDEN | 0.00021 | 0.00092 | 0.00029 | 143 | 143 | 186 | 0.2 |
| 1027 | ODES EHV | 1051 | HUNTSMAN | 0.00096 | 0.00539 | 0.00193 | 248 | 248 | 248 | 1.5 |
| 1027 | ODES EHV | 1055 | NYLON T | 0.00267 | 0.01518 | 0.00435 | 143 | 143 | 214 | 3.9 |
| 1027 | ODES EHV | 1107 | MONAH 2T | 0.02893 | 0.16767 | 0.04649 | 210 | 210 | 214 | 42.5 |
| 1027 | ODES EHV | 1111 | BIG3OD T | 0.00299 | 0.017 | 0.00487 | 105 | 105 | 214 | 4.4 |
| 1027 | ODES EHV | 1126 | ODESSA 2 | 0.00201 | 0.00921 | 0.00257 | 186 | 186 | 186 | 2.3 |
| 1027 | ODES EHV | 1128 | LIQD AIR | 0.00019 | 0.00202 | 0.00063 | 215 | 215 | 326 | 0.5 |
| 1027 | ODES EHV | 1137 | T.I. T | 0.00321 | 0.03327 | 0.01046 | 191 | 191 | 326 | 8.9 |
| 1027 | ODES EHV | 1199 | ARCO C T | 0.02215 | 0.10398 | 0.02787 | 186 | 186 | 186 | 25.9 |
| 1032 | MRGN CRK | 1064 | SUN | 0.02799 | 0.13167 | 0.03518 | 186 | 186 | 186 | 32.8 |
| 1032 | MRGN CRK | 1318 | CHINAGRV | 0.01181 | 0.05601 | 0.01484 | 186 | 186 | 186 | 13.9 |
| 1032 | MRGN CRK | 1318 | CHINAGRV | 0.01173 | 0.05517 | 0.01481 | 186 | 186 | 186 | 13.8 |
| 1032 | MRGN CRK | 1332 | COSDEN | 0.04118 | 0.12398 | 0.0378 | 143 | 143 | 155 | 32.2 |
| 1032 | MRGN CRK | 1335 | FORSAN T | 0.03157 | 0.1492 | 0.03949 | 96 | 96 | 186 | 37 |
| 1032 | MRGN CRK | 1341 | SWTRDT T | 0.02202 | 0.12532 | 0.03514 | 186 | 186 | 186 | 31.9 |
| 1051 | HUNTSMAN | 1052 | REXALL | 0.00074 | 0.0046 | 0.00152 | 143 | 143 | 248 | 1.3 |
| 1052 | REXALL | 1053 | GEN RUBR | 0.00045 | 0.00209 | 0.00058 | 143 | 143 | 186 | 0.5 |
| 1053 | GEN RUBR | 1054 | OLFN/SHL | 0.00113 | 0.00295 | 0.00071 | 124 | 124 | 124 | 0.7 |
| 1053 | GEN RUBR | 1099 | SWPORT T | 0.01284 | 0.06055 | 0.01609 | 186 | 186 | 186 | 15 |
| 1054 | OLFN/SHL | 1055 | NYLON T | 0.00108 | 0.0028 | 0.00069 | 124 | 124 | 124 | 0.7 |
| 1055 | NYLON T | 1056 | NYLON | 0.00156 | 0.00501 | 0.00132 | 124 | 124 | 124 | 1.2 |
| 1059 | MIDESSA | 1117 | MIDLND W | 0.00137 | 0.01423 | 0.00447 | 191 | 191 | 326 | 3.8 |
| 1059 | MIDESSA | 1120 | MID AIRP | 0.00606 | 0.02573 | 0.00659 | 143 | 143 | 162 | 6.2 |
| 1059 | MIDESSA | 1138 | T.I. | 0.00465 | 0.02188 | 0.00585 | 186 | 186 | 186 | 5.4 |
| 1064 | SUN | 1311 | SACROC | 0.00151 | 0.00709 | 0.0019 | 143 | 143 | 186 | 1.8 |
| 1064 | SUN | 1315 | BRAND | 0.00289 | 0.01361 | 0.00364 | 186 | 186 | 186 | 3.4 |
| 1074 | WINK SS | 1087 | WRDGLF T | 0.01301 | 0.04681 | 0.02389 | 143 | 143 | 248 | 16.1 |
| 1074 | WINK SS | 1092 | LOVING | 0.05162 | 0.08148 | 0.0163 | 84 | 84 | 84 | 16.6 |
| 1074 | WINK SS | 1147 | CHEYEN T | 0.01308 | 0.05417 | 0.01416 | 180 | 180 | 180 | 13.3 |
| 1074 | WINK SS | 37900 | WINK | 0.00096 | 0.00569 | 0.00152 | 144 | 144 | 218 | 1.4 |
| 1087 | WRDGLF T | 1089 | WICKET T | 0.00161 | 0.00422 | 0.00102 | 124 | 124 | 124 | 1 |
| 1088 | WICKETT | 1089 | WICKET T | 0.0037 | 0.0097 | 0.00234 | 124 | 124 | 124 | 2.3 |
| 1089 | WICKET T | 1091 | WARDGULF | 0.00777 | 0.02036 | 0.00491 | 124 | 124 | 124 | 4.8 |
| 1092 | LOVING | 1093 | EL MAR | 0.03653 | 0.05766 | 0.01153 | 84 | 84 | 84 | 11.7 |
| 1093 | EL MAR | 1094 | MASON | 0.03647 | 0.05756 | 0.01151 | 84 | 84 | 84 | 11.7 |
| 1094 | MASON | 1095 | SCRWBEAN | 0.04182 | 0.06601 | 0.0132 | 84 | 84 | 84 | 13.4 |
| 1095 | SCRWBEAN | 1096 | BLACKRVR | 0.04459 | 0.07038 | 0.01408 | 84 | 84 | 84 | 14.3 |
| 1096 | BLACKRVR | 1097 | TWPP MTR | 0.00844 | 0.02214 | 0.0054 | 124 | 124 | 124 | 5.2 |
| 1097 | TWPP MTR | 7387 | KUNITZ13 | 0.04479 | 0.11767 | 0.02795 | 103 | 103 | 127 | 27.9 |
| 1098 | KWIND RO | 7387 | KUNITZ13 | 0 | 0.0001 | 0 | 0 | 0 | 0 | 0 |
| 1099 | SWPORT T | 1100 | SW PORTL | 0.00238 | 0.00624 | 0.00151 | 124 | 124 | 124 | 1.5 |
| 1099 | SWPORT T | 1101 | EDWARDS | 0.01027 | 0.02685 | 0.0065 | 124 | 124 | 124 | 6.4 |
| 1099 | SWPORT T | 1102 | JUDKINS | 0.00337 | 0.01586 | 0.00424 | 143 | 143 | 186 | 3.9 |
| 1102 | JUDKINS | 1103 | SANDHL T | 0.00568 | 0.02669 | 0.00714 | 186 | 186 | 186 | 6.6 |
| 1103 | SANDHL T | 1104 | SANDHILL | 0.03588 | 0.05663 | 0.01133 | 84 | 84 | 84 | 11.5 |
| 1103 | SANDHL T | 1105 | MONAH 1T | 0.01463 | 0.0688 | 0.01839 | 186 | 186 | 186 | 17.1 |
| 1105 | MONAH 1T | 1106 | MONAHN 1 | 0.01211 | 0.01854 | 0.00421 | 84 | 84 | 84 | 4 |
| 1107 | MONAH 2T | 1108 | MONAHN 2 | 0.0027 | 0.00647 | 0.00186 | 124 | 124 | 124 | 1.7 |
| 1111 | BIG3OD T | 1112 | BIG 3 OD | 0.00168 | 0.00431 | 0.00108 | 124 | 124 | 124 | 1 |
| 1111 | BIG3OD T | 1113 | ODESA SW | 0.00199 | 0.01131 | 0.00323 | 214 | 214 | 214 | 2.9 |
| 1116 | WINDWOOD | 1117 | MIDLND W | 0.00325 | 0.01387 | 0.00351 | 143 | 143 | 162 | 3.3 |
| 1118 | CRMWD8 T | 1119 | CRMWD-8 | 0.00219 | 0.00573 | 0.00138 | 124 | 124 | 124 | 1.4 |
| 1118 | CRMWD8 T | 1120 | MID AIRP | 0.00069 | 0.00292 | 0.00075 | 143 | 143 | 162 | 0.7 |
| 1118 | CRMWD8 T | 1121 | GLENHAVN | 0.0047 | 0.01997 | 0.00511 | 143 | 143 | 162 | 4.8 |
| 1121 | GLENHAVN | 1127 | ODESSA 1 | 0.00151 | 0.01565 | 0.00492 | 287 | 287 | 326 | 4.2 |
| 1122 | ODESSA N | 1126 | ODESSA 2 | 0.00491 | 0.02849 | 0.00795 | 143 | 143 | 211 | 7.2 |
| 1122 | ODESSA N | 1130 | AM SFOST | 0.00295 | 0.0173 | 0.00472 | 143 | 143 | 211 | 4.3 |
| 1127 | ODESSA 1 | 1128 | LIQD AIR | 0.00066 | 0.00683 | 0.00215 | 326 | 326 | 326 | 1.8 |
| 1129 | WESTOVER | 1130 | AM SFOST | 0.00045 | 0.00264 | 0.00071 | 143 | 143 | 211 | 0.6 |
| 1132 | MIDL DWN | 1329 | SPRABERY | 0.01315 | 0.06179 | 0.01655 | 186 | 186 | 186 | 15.4 |
| 1137 | T.I. T | 1138 | T.I. | 0.00509 | 0.02393 | 0.00639 | 186 | 186 | 186 | 5.9 |
| 1137 | T.I. T | 1329 | SPRABERY | 0.01207 | 0.05702 | 0.01509 | 105 | 105 | 186 | 14.1 |
| 1141 | HOLT SS | 1143 | AMOCNC T | 0.00444 | 0.02084 | 0.00558 | 143 | 143 | 186 | 5.2 |
| 1141 | HOLT SS | 1145 | AM GLDSM | 0.00606 | 0.0285 | 0.00762 | 143 | 143 | 186 | 7.1 |
| 1141 | HOLT SS | 1281 | AMMIDF T | 0.00363 | 0.01706 | 0.00456 | 186 | 186 | 186 | 4.2 |
| 1143 | AMOCNC T | 1144 | AM NCOWD | 0.0037 | 0.00968 | 0.00234 | 124 | 124 | 124 | 2.3 |
| 1146 | YORK IPP | 1147 | CHEYEN T | 0.00686 | 0.02844 | 0.00744 | 143 | 143 | 180 | 7 |
| 1146 | YORK IPP | 1149 | DOLRHIDE | 0.00686 | 0.02844 | 0.00744 | 143 | 143 | 180 | 7 |
| 1147 | CHEYEN T | 1148 | CHEYENNE | 0.00467 | 0.01223 | 0.00295 | 124 | 124 | 124 | 2.9 |
| 1149 | DOLRHIDE | 1150 | AM 3BAR | 0.00556 | 0.02305 | 0.00603 | 143 | 143 | 180 | 5.7 |
| 1149 | DOLRHIDE | 1152 | UNOCAL | 0.0177 | 0.04533 | 0.0114 | 124 | 124 | 124 | 11.1 |
| 1150 | AM 3BAR | 1155 | ANDREW T | 0.01321 | 0.05474 | 0.01431 | 180 | 180 | 180 | 13.5 |
| 1155 | ANDREW T | 1156 | ANDREWS | 0.00362 | 0.00949 | 0.00228 | 124 | 124 | 124 | 2.2 |
| 1155 | ANDREW T | 1159 | N ANDREW | 0.0078 | 0.0323 | 0.00844 | 143 | 143 | 180 | 7.9 |
| 1159 | N ANDREW | 1161 | UN PKRBK | 0.00622 | 0.02926 | 0.00782 | 143 | 143 | 186 | 7.3 |
| 1159 | N ANDREW | 1165 | EXMEAN T | 0.00204 | 0.00844 | 0.00221 | 105 | 105 | 180 | 2.1 |
| 1161 | UN PKRBK | 1281 | AMMIDF T | 0.00895 | 0.04211 | 0.01125 | 186 | 186 | 186 | 10.5 |
| 1162 | LMESA LE | 1163 | LAMESA | 0 | 0.0001 | 0 | 0 | 0 | 0 | 0 |
| 1163 | LAMESA | 1168 | PAUL D T | 0.01921 | 0.07957 | 0.0208 | 96 | 96 | 180 | 19.6 |
| 1163 | LAMESA | 1307 | KEY LE | 0.00763 | 0.03589 | 0.00959 | 143 | 143 | 186 | 8.9 |
| 1165 | EXMEAN T | 1166 | EXMEANS | 0.00697 | 0.01826 | 0.0044 | 124 | 124 | 124 | 4.3 |
| 1165 | EXMEAN T | 1167 | MUSTANG | 0.01059 | 0.04386 | 0.01147 | 143 | 143 | 180 | 10.8 |
| 1167 | MUSTANG | 1168 | PAUL D T | 0.01191 | 0.04934 | 0.0129 | 143 | 143 | 180 | 12.1 |
| 1168 | PAUL D T | 1169 | PAUL DVS | 0.03644 | 0.05751 | 0.0115 | 84 | 84 | 84 | 11.7 |
| 1176 | GRANDVW | 1182 | MOCKNBRD | 0.01363 | 0.0774 | 0.02225 | 214 | 214 | 214 | 20 |
| 1177 | TEXMABEE | 1179 | TEX MA T | 0.01999 | 0.05229 | 0.01262 | 124 | 124 | 124 | 12.4 |
| 1178 | ADOBE MD | 1182 | MOCKNBRD | 0.00528 | 0.03002 | 0.0086 | 214 | 214 | 214 | 7.8 |
| 1179 | TEX MA T | 1180 | ECTR HIL | 0.01627 | 0.09245 | 0.02651 | 214 | 214 | 214 | 23.9 |
| 1179 | TEX MA T | 1184 | GODDARD | 0.00149 | 0.00848 | 0.00243 | 214 | 214 | 214 | 2.2 |
| 1197 | CRANE | 1199 | ARCO C T | 0.00509 | 0.02388 | 0.0064 | 143 | 143 | 186 | 5.9 |
| 1197 | CRANE | 1212 | UPTON | 0.00972 | 0.10083 | 0.03169 | 326 | 326 | 326 | 27 |
| 1197 | CRANE | 6615 | WTUCRAN4 | 0 | 0.0001 | 0 | 488 | 577 | 488 | 0 |
| 1197 | CRANE | 6615 | WTUCRAN4 | 0 | 0.0001 | 0 | 488 | 577 | 488 | 0 |
| 1199 | ARCO C T | 1201 | ARCO CRN | 0.01376 | 0.03605 | 0.0087 | 124 | 124 | 124 | 8.5 |
| 1210 | MIDKIFF | 1212 | UPTON | 0.00263 | 0.02726 | 0.00857 | 326 | 326 | 326 | 7.3 |
| 1210 | MIDKIFF | 1329 | SPRABERY | 0.0156 | 0.09068 | 0.02544 | 326 | 326 | 326 | 23 |
| 1281 | AMMIDF T | 1282 | AM MIDFM | 0.0121 | 0.03171 | 0.00766 | 124 | 124 | 124 | 7.5 |
| 1300 | EX SHARN | 1308 | GAIL LE | 0.01183 | 0.05564 | 0.01487 | 143 | 143 | 186 | 13.9 |
| 1300 | EX SHARN | 1309 | BLUFCK T | 0.00469 | 0.02208 | 0.0059 | 143 | 143 | 186 | 5.5 |
| 1300 | EX SHARN | 6191 | EXSHRN4 | 0 | 0.0001 | 0 | 0 | 0 | 0 | 0 |
| 1305 | SNYDER | 1311 | SACROC | 0.00819 | 0.03847 | 0.01031 | 143 | 143 | 186 | 9.6 |
| 1305 | SNYDER | 1318 | CHINAGRV | 0.01239 | 0.05818 | 0.01559 | 143 | 143 | 186 | 14.5 |
| 1307 | KEY LE | 1308 | GAIL LE | 0.02034 | 0.09566 | 0.02557 | 143 | 143 | 186 | 23.8 |
| 1309 | BLUFCK T | 1310 | KNAPP | 0.0038 | 0.01783 | 0.00478 | 186 | 186 | 186 | 4.4 |
| 1309 | BLUFCK T | 1318 | CHINAGRV | 0.01092 | 0.05138 | 0.01373 | 186 | 186 | 186 | 12.8 |
| 1310 | KNAPP | 1312 | SCURY CH | 0.0148 | 0.05138 | 0.01315 | 124 | 124 | 124 | 12.5 |
| 1312 | SCURY CH | 1313 | ENISCK T | 0.00196 | 0.00514 | 0.00124 | 124 | 124 | 124 | 1.2 |
| 1313 | ENISCK T | 1314 | ENNIS CK | 0.00274 | 0.00717 | 0.00173 | 124 | 124 | 124 | 1.7 |
| 1313 | ENISCK T | 1315 | BRAND | 0.00235 | 0.01104 | 0.00295 | 143 | 143 | 186 | 2.8 |
| 1314 | ENNIS CK | 1410 | ENSCRKSS | 0 | 0.0001 | 0 | 124 | 124 | 124 | 0 |
| 1318 | CHINAGRV | 1394 | GTTY V T | 0.02024 | 0.09522 | 0.02544 | 186 | 186 | 186 | 23.7 |
| 1318 | CHINAGRV | 1398 | RADIUM M | 0.04843 | 0.22785 | 0.06088 | 105 | 105 | 186 | 56.8 |
| 1322 | BIG SPRG | 1324 | BIG SPGW | 0.02469 | 0.03523 | 0.0087 | 84 | 84 | 84 | 7.9 |
| 1322 | BIG SPRG | 1332 | COSDEN | 0.00154 | 0.00392 | 0.00128 | 143 | 143 | 167 | 1 |
| 1322 | BIG SPRG | 1394 | GTTY V T | 0.01277 | 0.05608 | 0.01498 | 96 | 96 | 186 | 14 |
| 1324 | BIG SPGW | 1325 | AIR PARK | 0.00322 | 0.00843 | 0.00206 | 124 | 124 | 124 | 2 |
| 1329 | SPRABERY | 1337 | CRMWD7 T | 0.00162 | 0.00767 | 0.00203 | 143 | 143 | 186 | 1.9 |
| 1335 | FORSAN T | 1336 | FORSAN | 0.00529 | 0.01387 | 0.00335 | 124 | 124 | 124 | 3.3 |
| 1335 | FORSAN T | 1337 | CRMWD7 T | 0.02892 | 0.13665 | 0.03617 | 143 | 143 | 186 | 33.9 |
| 1337 | CRMWD7 T | 1338 | CRMWD-7 | 0.00169 | 0.00443 | 0.00107 | 124 | 124 | 124 | 1 |
| 1339 | ESKOTA | 1341 | SWTRDT T | 0.00708 | 0.04073 | 0.01145 | 214 | 214 | 214 | 10.4 |
| 1339 | ESKOTA | 1343 | TRENTIPP | 0.00217 | 0.01262 | 0.00354 | 214 | 214 | 214 | 3.2 |
| 1339 | ESKOTA | 6260 | ABSOUTH4 | 0.02056 | 0.11947 | 0.0335 | 214 | 214 | 214 | 30.3 |
| 1341 | SWTRDT T | 1342 | SWWTR DT | 0.00281 | 0.00674 | 0.00194 | 124 | 124 | 124 | 1.8 |
| 1355 | ACKRLY V | 1395 | GETTY VL | 0.03267 | 0.08559 | 0.02065 | 48 | 48 | 124 | 20.3 |
| 1371 | MURRAY M | 1431 | GRAHAM P | 0.01618 | 0.07599 | 0.02037 | 96 | 96 | 186 | 19 |
| 1371 | MURRAY M | 6169 | PTCRK2 4 | 0.03368 | 0.15744 | 0.04203 | 155 | 155 | 155 | 39.2 |
| 1394 | GTTY V T | 1395 | GETTY VL | 0.01815 | 0.04756 | 0.01148 | 124 | 124 | 124 | 11.3 |
| 1398 | RADIUM M | 6161 | PTCRK1 4 | 0.02837 | 0.13247 | 0.03536 | 155 | 155 | 155 | 33 |
| 1423 | BOWMAN A | 1446 | LK WICH | 0.00384 | 0.0218 | 0.00624 | 210 | 210 | 214 | 5.6 |
| 1423 | BOWMAN A | 1499 | PARKWY E | 0.00234 | 0.0142 | 0.00356 | 214 | 214 | 214 | 3.4 |
| 1424 | BOWMAN B | 1431 | GRAHAM P | 0.03162 | 0.19148 | 0.04809 | 210 | 210 | 214 | 46.4 |
| 1424 | BOWMAN B | 1464 | S WFALLS | 0.00489 | 0.02811 | 0.00791 | 191 | 191 | 214 | 7.2 |
| 1424 | BOWMAN B | 1500 | PARKWY W | 0.00234 | 0.0142 | 0.00356 | 214 | 214 | 214 | 3.4 |
| 1426 | FISHRDSS | 1427 | FISHR RD | 0.00002 | 0.001 | 0.00008 | 287 | 287 | 339 | 0.1 |
| 1426 | FISHRDSS | 1483 | CITYVIEW | 0.00606 | 0.0376 | 0.01109 | 143 | 143 | 214 | 9.8 |
| 1427 | FISHR RD | 1448 | WFALLS | 0.00168 | 0.01283 | 0.00403 | 283 | 283 | 283 | 3.4 |
| 1431 | GRAHAM P | 1477 | RICE | 0.0077 | 0.03232 | 0.01173 | 186 | 186 | 186 | 9.3 |
| 1431 | GRAHAM P | 1601 | GRAHAM E | 0.00454 | 0.02112 | 0.00578 | 251 | 251 | 251 | 5.3 |
| 1431 | GRAHAM P | 1613 | BRECK T | 0.0236 | 0.11166 | 0.02987 | 105 | 105 | 186 | 27.8 |
| 1431 | GRAHAM P | 1616 | SUNECH T | 0.0157 | 0.07386 | 0.01974 | 186 | 186 | 186 | 18.4 |
| 1441 | CMCHE SS | 1650 | CMCHE T | 0.00296 | 0.01652 | 0.00458 | 186 | 186 | 186 | 4.2 |
| 1441 | CMCHE SS | 1654 | ZEPHYR M | 0.01482 | 0.08611 | 0.02415 | 214 | 214 | 214 | 21.8 |
| 1441 | CMCHE SS | 1661 | BRNWD | 0.02449 | 0.11782 | 0.03154 | 186 | 186 | 186 | 29.4 |
| 1446 | LK WICH | 1464 | S WFALLS | 0.00269 | 0.00969 | 0.00495 | 249 | 249 | 249 | 3.3 |
| 1446 | LK WICH | 1494 | WF HOSP | 0.00042 | 0.00437 | 0.00143 | 287 | 287 | 339 | 1.2 |
| 1448 | WFALLS | 1480 | RATHGBER | 0.00354 | 0.01671 | 0.00442 | 143 | 143 | 186 | 4.1 |
| 1450 | PLEASVAL | 1485 | ACROCH | 0.00455 | 0.02626 | 0.00733 | 143 | 143 | 214 | 6.7 |
| 1450 | PLEASVAL | 1492 | RVR BEND | 0.00134 | 0.01412 | 0.00462 | 339 | 339 | 339 | 3.9 |
| 1450 | PLEASVAL | 1498 | WF COGEN | 0.00381 | 0.02303 | 0.0058 | 214 | 214 | 214 | 5.6 |
| 1450 | PLEASVAL | 1499 | PARKWY E | 0.00373 | 0.02262 | 0.00567 | 214 | 214 | 214 | 5.5 |
| 1464 | S WFALLS | 1467 | NORTHSTR | 0.00456 | 0.02144 | 0.00573 | 186 | 186 | 186 | 5.3 |
| 1464 | S WFALLS | 1474 | SCOTLD M | 0.01065 | 0.03681 | 0.01849 | 143 | 143 | 249 | 12.6 |
| 1464 | S WFALLS | 1478 | AROHD M | 0.00028 | 0.00134 | 0.00036 | 143 | 143 | 186 | 0.3 |
| 1467 | NORTHSTR | 1468 | AROWHEAD | 0.00176 | 0.00827 | 0.00221 | 186 | 186 | 186 | 2 |
| 1468 | AROWHEAD | 1470 | NEWPRT M | 0.02906 | 0.13668 | 0.03653 | 186 | 186 | 186 | 33.9 |
| 1469 | SUNSET | 1470 | NEWPRT M | 0.00707 | 0.03324 | 0.00888 | 186 | 186 | 186 | 8.4 |
| 1469 | SUNSET | 1561 | ALVORD | 0.00963 | 0.04656 | 0.01252 | 143 | 143 | 186 | 11.6 |
| 1472 | NAVYK SS | 1475 | WINDTHOR | 0.01499 | 0.03918 | 0.0095 | 105 | 105 | 124 | 9.3 |
| 1474 | SCOTLD M | 1475 | WINDTHOR | 0.00414 | 0.015 | 0.00755 | 143 | 143 | 249 | 5.1 |
| 1475 | WINDTHOR | 1476 | MARKLEY | 0.00917 | 0.03321 | 0.01672 | 143 | 143 | 249 | 11.4 |
| 1476 | MARKLEY | 1477 | RICE | 0.00826 | 0.02991 | 0.01506 | 120 | 120 | 249 | 10.2 |
| 1478 | AROHD M | 1480 | RATHGBER | 0.0029 | 0.01367 | 0.00361 | 186 | 186 | 186 | 3.4 |
| 1483 | CITYVIEW | 1487 | HEMMERD | 0.00184 | 0.01065 | 0.00295 | 143 | 143 | 214 | 2.5 |
| 1484 | PPG | 1485 | ACROCH | 0.00095 | 0.00552 | 0.00153 | 96 | 96 | 214 | 1.4 |
| 1484 | PPG | 1487 | HEMMERD | 0.00025 | 0.00145 | 0.0004 | 96 | 96 | 214 | 0.6 |
| 1485 | ACROCH | 1486 | BOOMTOWN | 0.00536 | 0.01404 | 0.00339 | 124 | 124 | 124 | 3.3 |
| 1489 | SIKES | 1493 | ARTHR ST | 0.00075 | 0.00783 | 0.00257 | 339 | 339 | 339 | 2.1 |
| 1489 | SIKES | 1494 | WF HOSP | 0.00003 | 0.001 | 0.00011 | 339 | 339 | 339 | 0.1 |
| 1492 | RVR BEND | 1493 | ARTHR ST | 0.00096 | 0.01012 | 0.00332 | 339 | 339 | 339 | 2.8 |
| 1496 | CERTEEDW | 1498 | WF COGEN | 0.00019 | 0.001 | 0.00012 | 124 | 124 | 124 | 0.1 |
| 1497 | CERTEEDE | 1498 | WF COGEN | 0.00005 | 0.001 | 0.00003 | 124 | 124 | 124 | 0.1 |
| 1498 | WF COGEN | 1500 | PARKWY W | 0.00017 | 0.001 | 0.00027 | 214 | 214 | 214 | 0.2 |
| 1561 | ALVORD | 1562 | CHCO W T | 0.00395 | 0.02292 | 0.00642 | 191 | 191 | 214 | 5.8 |
| 1562 | CHCO W T | 1563 | CHCO W | 0.00096 | 0.00454 | 0.00122 | 186 | 186 | 186 | 1.1 |
| 1562 | CHCO W T | 1564 | CHCO GH | 0.00061 | 0.00289 | 0.00078 | 186 | 186 | 186 | 0.7 |
| 1564 | CHCO GH | 1565 | BRDGPORT | 0.0027 | 0.0128 | 0.00335 | 186 | 186 | 186 | 3.2 |
| 1565 | BRDGPORT | 1566 | DECATUR | 0.01077 | 0.0507 | 0.01373 | 186 | 186 | 186 | 12.6 |
| 1566 | DECATUR | 1570 | RHOME | 0.0117 | 0.0523 | 0.0137 | 124 | 124 | 124 | 13.1 |
| 1570 | RHOME | 1860 | EAGLE MT | 0.01042 | 0.04991 | 0.01344 | 186 | 186 | 186 | 12.5 |
| 1571 | ORAN | 1575 | MINWL W | 0.00708 | 0.02554 | 0.01324 | 249 | 249 | 249 | 8.8 |
| 1571 | ORAN | 1592 | WTHFRD | 0.02229 | 0.10533 | 0.02788 | 186 | 186 | 186 | 26.1 |
| 1571 | ORAN | 1596 | GRAHAMSS | 0.02405 | 0.11365 | 0.03008 | 186 | 186 | 186 | 28.1 |
| 1574 | PALOPNTO | 1576 | MINWLJCT | 0.00248 | 0.02567 | 0.00807 | 350 | 350 | 350 | 6.9 |
| 1574 | PALOPNTO | 1578 | PALOPT M | 0.00106 | 0.011 | 0.00346 | 350 | 350 | 350 | 2.9 |
| 1575 | MINWL W | 1576 | MINWLJCT | 0.00092 | 0.00331 | 0.00171 | 249 | 249 | 249 | 1.1 |
| 1576 | MINWLJCT | 1577 | MINWL 2 | 0.00347 | 0.01997 | 0.0057 | 249 | 249 | 249 | 5.1 |
| 1577 | MINWL 2 | 1580 | MINWL 1 | 0 | 0.0001 | 0 | 214 | 214 | 214 | 0 |
| 1591 | SPRGTOWN | 1592 | WTHFRD | 0.00905 | 0.02374 | 0.0058 | 124 | 124 | 124 | 5.6 |
| 1592 | WTHFRD | 2062 | AZLE | 0.00982 | 0.04687 | 0.01219 | 143 | 143 | 186 | 11.5 |
| 1596 | GRAHAMSS | 1601 | GRAHAM E | 0.00154 | 0.00705 | 0.00199 | 251 | 251 | 251 | 1.8 |
| 1612 | BRECK N | 1614 | BRECK | 0.00756 | 0.03557 | 0.00951 | 143 | 143 | 186 | 8.9 |
| 1612 | BRECK N | 1616 | SUNECH T | 0.01238 | 0.05825 | 0.01557 | 186 | 186 | 186 | 14.5 |
| 1613 | BRECK T | 1614 | BRECK | 0.01923 | 0.05038 | 0.01216 | 124 | 124 | 124 | 11.9 |
| 1613 | BRECK T | 1618 | CADDO | 0.00055 | 0.00257 | 0.00069 | 143 | 143 | 186 | 0.6 |
| 1616 | SUNECH T | 1617 | SUN ECH | 0.00135 | 0.00354 | 0.00085 | 124 | 124 | 124 | 0.8 |
| 1618 | CADDO | 1619 | COLNY CK | 0.01556 | 0.07322 | 0.01957 | 186 | 186 | 186 | 18.2 |
| 1619 | COLNY CK | 1624 | LEON | 0.0059 | 0.02778 | 0.00742 | 120 | 120 | 186 | 6.9 |
| 1624 | LEON | 1640 | LNGLVL M | 0.06053 | 0.09578 | 0.01905 | 84 | 84 | 84 | 19.5 |
| 1624 | LEON | 6309 | PUTNAM 4 | 0.08643 | 0.1417 | 0.03101 | 72 | 72 | 79 | 30.9 |
| 1636 | DUBLIN | 1641 | STPHVIL | 0.00969 | 0.03494 | 0.01813 | 248 | 248 | 248 | 12 |
| 1636 | DUBLIN | 1649 | HASSE M | 0.012 | 0.05652 | 0.01504 | 186 | 186 | 186 | 14.1 |
| 1640 | LNGLVL M | 1641 | STPHVIL | 0.04088 | 0.06926 | 0.01428 | 84 | 84 | 84 | 14.4 |
| 1641 | STPHVIL | 1644 | SELDEN M | 0.00324 | 0.01866 | 0.00521 | 191 | 191 | 214 | 4.8 |
| 1641 | STPHVIL | 2278 | CPK STUP | 0.01971 | 0.11328 | 0.03168 | 214 | 214 | 214 | 28.8 |
| 1644 | SELDEN M | 1645 | JOHNVL M | 0.03822 | 0.06341 | 0.01308 | 84 | 84 | 84 | 13.2 |
| 1645 | JOHNVL M | 1646 | WALNUTSP | 0.03799 | 0.05984 | 0.01201 | 84 | 84 | 84 | 12.2 |
| 1649 | HASSE M | 1650 | CMCHE T | 0.00529 | 0.02493 | 0.00663 | 186 | 186 | 186 | 6.2 |
| 1650 | CMCHE T | 1651 | CMCHE | 0.00069 | 0.00325 | 0.00087 | 186 | 186 | 186 | 0.8 |
| 1654 | ZEPHYR M | 1655 | BRNWD SS | 0.00327 | 0.019 | 0.00533 | 191 | 191 | 214 | 4.8 |
| 1655 | BRNWD SS | 7070 | GOLDTH13 | 0.04572 | 0.12402 | 0.03008 | 124 | 124 | 124 | 29.5 |
| 1655 | BRNWD SS | 7386 | CAMPBO13 | 0.00487 | 0.01671 | 0.00433 | 124 | 124 | 124 | 3.5 |
| 1656 | BRNWD S | 1661 | BRNWD | 0.00409 | 0.01918 | 0.0052 | 186 | 186 | 186 | 4.8 |
| 1656 | BRNWD S | 7386 | CAMPBO13 | 0.00531 | 0.01392 | 0.00338 | 124 | 124 | 124 | 3.9 |
|  |  |  |  |  |  | 2.63682 |  |  |  |  |

Appendix C AEP 345kV Line Charging

| X------FROM------X X-------TO-------X Z S |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| BUS# | NAME | BUS# | NAME | LINE R | LINE X | CHRGING | RATEA | RATEB | RATEC | LENGTH |
| 1030 | MRGN CRK | 6009 | TWBT7 | 0.0021 | 0.03619 | 0.66499 | 1515 | 1770 | 1515 | 75 |
| 1050 | ENRONIPP | 6235 | ABMULCW7 | 0.00179 | 0.01556 | 0.2922 | 717 | 717 | 1072 | 32.7 |
| 1425 | FISHRDSS | 6100 | OKLAEHV7 | 0.00291 | 0.02641 | 0.43348 | 717 | 717 | 1072 | 52 |
| 1430 | GRAHAM | 6230 | ABMULCE7 | 0.00459 | 0.03987 | 0.74847 | 717 | 717 | 1072 | 83.7 |
| 1440 | CMCHE SS | 6444 | SAREDCK7 | 0.00338 | 0.05793 | 1.08416 | 1515 | 1770 | 1515 | 121.3 |
| 6009 | TWBT7 | 6444 | SAREDCK7 | 0.00053 | 0.00925 | 0.16516 | 1515 | 1770 | 1515 | 18.9 |
| 6096 | NORTHDC7 | 6100 | OKLAEHV7 | 0 | 0.001 | 0 | 300 | 300 | 300 | 0 |
| 6100 | OKLAEHV7 | 6235 | ABMULCW7 | 0.00637 | 0.05805 | 0.98616 | 1011 | 1176 | 1011 | 115.5 |
| 6230 | ABMULCE7 | 6235 | ABMULCW7 | 0 | 0.0001 | 0 | 1219 | 1444 | 1219 | 0 |
| 6230 | ABMULCE7 | 6444 | SAREDCK7 | 0.0042 | 0.03825 | 0.64983 | 1011 | 1176 | 1011 | 76.1 |
|  |  |  |  |  |  | 5.02445 |  |  |  |  |

Appendix D AEP 138kV Line Charging

| X------FROM------X X-------TO-------X Z S |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| BUS# | NAME | BUS# | NAME | LINE R | LINE X | CHRGING | RATEA | RATEB | RATEC | LENGTH |
| 512 | NWTHRFRD | 6696 | NTWTHFRD | 0 | 0.0001 | 0 | 0 | 0 | 0 | 0 |
| 743 | SALTCK4 | 6150 | SPUR 4 | 0.0123 | 0.0696 | 0.01952 | 202 | 235 | 202 | 17.8 |
| 1010 | PERMIANB | 6655 | BARRILA4 | 0.0593 | 0.2131 | 0.05479 | 147 | 155 | 147 | 52.2 |
| 1197 | CRANE | 6615 | WTUCRAN4 | 0 | 0.0001 | 0 | 488 | 577 | 488 | 0 |
| 1197 | CRANE | 6615 | WTUCRAN4 | 0 | 0.0001 | 0 | 488 | 577 | 488 | 0 |
| 1300 | EX SHARN | 6191 | EXSHRN4 | 0 | 0.0001 | 0 | 0 | 0 | 0 | 0 |
| 1339 | ESKOTA | 6260 | ABSOUTH4 | 0.0206 | 0.1195 | 0.0335 | 214 | 214 | 214 | 30.3 |
| 1371 | MURRAY M | 6169 | PTCRK2 4 | 0.0337 | 0.1574 | 0.04203 | 155 | 155 | 155 | 39.2 |
| 1398 | RADIUM M | 6161 | PTCRK1 4 | 0.0284 | 0.1325 | 0.03536 | 155 | 155 | 155 | 33 |
| 1624 | LEON | 6309 | PUTNAM 4 | 0.0864 | 0.1417 | 0.03101 | 72 | 72 | 79 | 30.9 |
| 6014 | SWMTP4 | 6015 | SWMESA4 | 0.0032 | 0.0105 | 0.0031 | 147 | 170 | 147 | 2.8 |
| 6014 | SWMTP4 | 6536 | BIGLAK24 | 0.0467 | 0.167 | 0.04301 | 147 | 170 | 147 | 40.9 |
| 6014 | SWMTP4 | 60009 | KM ETP4 | 0.0003 | 0.0009 | 0.00024 | 147 | 170 | 147 | 0.2 |
| 6019 | ORNNWPT4 | 6022 | INDM1 T4 | 0.009 | 0.0232 | 0.00565 | 117 | 136 | 117 | 5.5 |
| 6019 | ORNNWPT4 | 6584 | INDMESA2 | 0.009 | 0.0232 | 0.00565 | 117 | 136 | 117 | 5.5 |
| 6021 | INDM1PP4 | 6022 | INDM1 T4 | 0.0017 | 0.0095 | 0.00286 | 206 | 240 | 206 | 2.5 |
| 6022 | INDM1 T4 | 6582 | MVIEWSW2 | 0.0113 | 0.0293 | 0.00713 | 117 | 136 | 117 | 7 |
| 6030 | CHILD4WT | 6135 | PADCLA 4 | 0.0358 | 0.1279 | 0.03308 | 147 | 170 | 147 | 31.4 |
| 6050 | LKPAULS4 | 6060 | VRNMAIN4 | 0.0279 | 0.0994 | 0.02562 | 147 | 170 | 147 | 24.4 |
| 6050 | LKPAULS4 | 6110 | EMUNDY24 | 0.085 | 0.1748 | 0.08232 | 158 | 192 | 158 | 57 |
| 6060 | VRNMAIN4 | 6097 | OKLEHV14 | 0.0064 | 0.0359 | 0.01027 | 202 | 235 | 202 | 9.3 |
| 6066 | SW VERN4 | 6098 | OKLEHV24 | 0.0052 | 0.0293 | 0.0082 | 202 | 235 | 202 | 7.5 |
| 6097 | OKLEHV14 | 6098 | OKLEHV24 | 0 | 0.0001 | 0 | 488 | 577 | 488 | 0 |
| 6110 | EMUNDY24 | 6117 | EMUNDY14 | 0 | 0.0001 | 0 | 488 | 577 | 488 | 0 |
| 6110 | EMUNDY24 | 6169 | PTCRK2 4 | 0.0305 | 0.1089 | 0.02801 | 147 | 170 | 147 | 26.7 |
| 6117 | EMUNDY14 | 6135 | PADCLA 4 | 0.0711 | 0.2537 | 0.06546 | 147 | 170 | 147 | 62.3 |
| 6117 | EMUNDY14 | 6161 | PTCRK1 4 | 0.0356 | 0.1075 | 0.02686 | 131 | 151 | 131 | 26 |
| 6150 | SPUR 4 | 6158 | ASPERMT4 | 0.0517 | 0.1867 | 0.04783 | 144 | 167 | 144 | 45.5 |
| 6158 | ASPERMT4 | 6161 | PTCRK1 4 | 0.0454 | 0.1621 | 0.04174 | 147 | 170 | 147 | 39.7 |
| 6161 | PTCRK1 4 | 6165 | CALCRKTP | 0.0033 | 0.0116 | 0.00298 | 147 | 170 | 147 | 2.8 |
| 6161 | PTCRK1 4 | 6169 | PTCRK2 4 | 0 | 0.0001 | 0 | 488 | 577 | 488 | 0 |
| 6165 | CALCRKTP | 6166 | CAL CRK | 5E-05 | 7E-05 | 0.00002 | 79 | 96 | 79 | 0 |
| 6165 | CALCRKTP | 6222 | PHATM W4 | 0.0409 | 0.1481 | 0.03823 | 147 | 170 | 147 | 36.4 |
| 6169 | PTCRK2 4 | 6228 | ABILNW14 | 0.0507 | 0.1812 | 0.04669 | 147 | 170 | 147 | 44.4 |
| 6222 | PHATM W4 | 6223 | ABRAINY4 | 0.0022 | 0.0186 | 0.00811 | 260 | 304 | 260 | 5.9 |
| 6222 | PHATM W4 | 6226 | ABEASTP | 0.0052 | 0.0293 | 0.01287 | 260 | 304 | 260 | 9.4 |
| 6222 | PHATM W4 | 6291 | ABAILEN4 | 0.0048 | 0.0277 | 0.00768 | 202 | 235 | 202 | 7.1 |
| 6223 | ABRAINY4 | 6228 | ABILNW14 | 0.0017 | 0.015 | 0.00727 | 404 | 470 | 404 | 5.1 |
| 6226 | ABEASTP | 6275 | ABEAST24 | 0.0011 | 0.0061 | 0.0028 | 293 | 340 | 293 | 2 |
| 6226 | ABEASTP | 6292 | ABCOCLB4 | 0.0038 | 0.0213 | 0.00615 | 202 | 235 | 202 | 5.5 |
| 6228 | ABILNW14 | 6232 | ABMULCK4 | 0.0012 | 0.0099 | 0.0029 | 260 | 304 | 260 | 2.6 |
| 6228 | ABILNW14 | 6255 | ABELMCK4 | 0.0021 | 0.0119 | 0.0034 | 202 | 235 | 202 | 3.1 |
| 6228 | ABILNW14 | 6335 | OAKCK1 4 | 0.0652 | 0.1989 | 0.04987 | 131 | 151 | 131 | 48.1 |
| 6231 | ABMULC24 | 6232 | ABMULCK4 | 0 | 0.0001 | 0 | 488 | 577 | 488 | 0 |
| 6231 | ABMULC24 | 6772 | ABINOPK4 | 0.0018 | 0.0158 | 0.00461 | 260 | 304 | 260 | 4.1 |
| 6255 | ABELMCK4 | 6256 | ABTWILT4 | 0.0033 | 0.0181 | 0.00542 | 202 | 235 | 202 | 4.8 |
| 6255 | ABELMCK4 | 6772 | ABINOPK4 | 0.0007 | 0.0061 | 0.00183 | 260 | 304 | 260 | 1.6 |
| 6256 | ABTWILT4 | 6257 | ABREBLN4 | 0.0013 | 0.0071 | 0.00198 | 202 | 235 | 202 | 1.8 |
| 6257 | ABREBLN4 | 6261 | ABWYLIE4 | 0.0014 | 0.0081 | 0.00227 | 202 | 235 | 202 | 2.1 |
| 6260 | ABSOUTH4 | 6261 | ABWYLIE4 | 0.0011 | 0.0064 | 0.00182 | 202 | 235 | 202 | 1.6 |
| 6260 | ABSOUTH4 | 6290 | ABMAPLE4 | 0.0033 | 0.0187 | 0.00532 | 202 | 235 | 202 | 4.8 |
| 6260 | ABSOUTH4 | 6293 | ABCNYRK4 | 0.0013 | 0.0076 | 0.00213 | 202 | 235 | 202 | 1.9 |
| 6260 | ABSOUTH4 | 6313 | POTOSITP | 0.0225 | 0.0345 | 0.00739 | 79 | 96 | 79 | 7.5 |
| 6260 | ABSOUTH4 | 6335 | OAKCK1 4 | 0.0279 | 0.1583 | 0.04433 | 202 | 235 | 202 | 40.4 |
| 6275 | ABEAST24 | 6290 | ABMAPLE4 | 0.0032 | 0.0176 | 0.00522 | 202 | 235 | 202 | 4.6 |
| 6275 | ABEAST24 | 6291 | ABAILEN4 | 0.0017 | 0.0096 | 0.0027 | 202 | 235 | 202 | 2.5 |
| 6292 | ABCOCLB4 | 6293 | ABCNYRK4 | 0.0009 | 0.005 | 0.00139 | 202 | 235 | 202 | 1.3 |
| 6309 | PUTNAM 4 | 6773 | PCANBYU4 | 0.0679 | 0.1117 | 0.02533 | 79 | 96 | 79 | 25.1 |
| 6313 | POTOSITP | 6314 | POTOSI | 0.0016 | 0.009 | 0.00278 | 202 | 235 | 202 | 2.4 |
| 6313 | POTOSITP | 6773 | PCANBYU4 | 0.0125 | 0.0191 | 0.0041 | 79 | 96 | 79 | 4.2 |
| 6324 | FTCHAD | 6325 | FTCHADTP | 6E-05 | 9E-05 | 0.00002 | 79 | 96 | 79 | 0 |
| 6325 | FTCHADTP | 6335 | OAKCK1 4 | 0.0032 | 0.0113 | 0.00291 | 147 | 170 | 147 | 2.8 |
| 6325 | FTCHADTP | 6340 | BALNGR 4 | 0.0331 | 0.1149 | 0.02942 | 131 | 151 | 131 | 28.1 |
| 6335 | OAKCK1 4 | 6425 | CDRHILL4 | 0.0787 | 0.1207 | 0.02582 | 79 | 96 | 79 | 26.4 |
| 6335 | OAKCK1 4 | 6441 | ORIENTR4 | 0.0354 | 0.1133 | 0.02861 | 131 | 151 | 131 | 27.5 |
| 6340 | BALNGR 4 | 6360 | IVEYPTP4 | 0.0137 | 0.0489 | 0.01262 | 147 | 170 | 147 | 12 |
| 6340 | BALNGR 4 | 6458 | CRMWD2 | 0.0218 | 0.0777 | 0.01998 | 147 | 170 | 147 | 19 |
| 6347 | COLETAP4 | 6348 | COLEMAN4 | 0.0034 | 0.0122 | 0.00313 | 147 | 170 | 147 | 3 |
| 6347 | COLETAP4 | 6355 | SANANNA4 | 0.0062 | 0.0222 | 0.0057 | 147 | 170 | 147 | 5.4 |
| 6347 | COLETAP4 | 6360 | IVEYPTP4 | 0.0239 | 0.0855 | 0.022 | 147 | 170 | 147 | 21 |
| 6360 | IVEYPTP4 | 6361 | IVEYPMP4 | 0.0137 | 0.0511 | 0.01312 | 149 | 173 | 149 | 12.5 |
| 6360 | IVEYPTP4 | 6362 | IVEYBST4 | 0.012 | 0.045 | 0.01155 | 149 | 173 | 149 | 11 |
| 6375 | MENARD 4 | 6390 | MASON4 | 0.042 | 0.1506 | 0.03871 | 147 | 170 | 147 | 36.9 |
| 6375 | MENARD 4 | 6480 | SAPS1 4 | 0.0632 | 0.2262 | 0.05833 | 147 | 170 | 147 | 55.5 |
| 6390 | MASON4 | 7132 | GILLES13 | 0.0361 | 0.149 | 0.039 | 147 | 170 | 147 | 37 |
| 6441 | ORIENTR4 | 6442 | SAREDCK4 | 0.0146 | 0.0438 | 0.01117 | 131 | 151 | 131 | 10.7 |
| 6442 | SAREDCK4 | 6447 | SAPLANN4 | 0.0044 | 0.0249 | 0.007 | 202 | 235 | 202 | 6.4 |
| 6442 | SAREDCK4 | 6449 | SACOKE 4 | 0.0055 | 0.031 | 0.00887 | 202 | 235 | 202 | 8 |
| 6442 | SAREDCK4 | 6458 | CRMWD2 | 0.0155 | 0.0546 | 0.01433 | 147 | 170 | 147 | 13.5 |
| 6442 | SAREDCK4 | 6473 | SABENFK4 | 0.0173 | 0.0614 | 0.01591 | 147 | 170 | 147 | 15.1 |
| 6447 | SAPLANN4 | 6464 | SANORTH4 | 0.0022 | 0.0126 | 0.00355 | 202 | 235 | 202 | 3.2 |
| 6448 | HIGHLAN4 | 6449 | SACOKE 4 | 0.0011 | 0.006 | 0.00167 | 202 | 235 | 202 | 1.5 |
| 6448 | HIGHLAN4 | 6452 | SACONCH4 | 0.0001 | 0.0008 | 0.00021 | 202 | 235 | 202 | 0.2 |
| 6452 | SACONCH4 | 6453 | SASOTAP4 | 0.0029 | 0.0102 | 0.00262 | 147 | 170 | 147 | 2.5 |
| 6453 | SASOTAP4 | 6454 | SASOUTH4 | 0.003 | 0.0045 | 0.001 | 79 | 96 | 79 | 1 |
| 6453 | SASOTAP4 | 6480 | SAPS1 4 | 0.0042 | 0.0151 | 0.0039 | 147 | 170 | 147 | 3.7 |
| 6464 | SANORTH4 | 6482 | SALKDRV4 | 0.0014 | 0.0078 | 0.0024 | 202 | 235 | 202 | 2.1 |
| 6470 | SACHWST4 | 6481 | SASLAND4 | 0.0015 | 0.0085 | 0.00237 | 202 | 235 | 202 | 2.2 |
| 6470 | SACHWST4 | 6482 | SALKDRV4 | 0.0045 | 0.0254 | 0.00709 | 202 | 235 | 202 | 6.5 |
| 6473 | SABENFK4 | 6483 | SAPS2 4 | 0.004 | 0.0144 | 0.00369 | 147 | 170 | 147 | 3.5 |
| 6480 | SAPS1 4 | 6481 | SASLAND4 | 0.0004 | 0.0023 | 0.00064 | 202 | 235 | 202 | 0.6 |
| 6480 | SAPS1 4 | 6483 | SAPS2 4 | 0 | 0.0001 | 0 | 488 | 577 | 488 | 0 |
| 6480 | SAPS1 4 | 6535 | BIGLAKE4 | 0.0705 | 0.2523 | 0.06512 | 147 | 170 | 147 | 61.9 |
| 6483 | SAPS2 4 | 6493 | PAVEPAW4 | 0.0354 | 0.1264 | 0.03252 | 147 | 170 | 147 | 31 |
| 6492 | PAVEPAW4 | 6493 | PAVEPAW4 | 0.0006 | 0.002 | 0.00052 | 147 | 170 | 147 | 0.5 |
| 6493 | PAVEPAW4 | 6500 | LIVEOAK4 | 0.0083 | 0.0296 | 0.00762 | 147 | 170 | 147 | 7.3 |
| 6500 | LIVEOAK4 | 6515 | SONORA 4 | 0.0252 | 0.0901 | 0.02317 | 147 | 170 | 147 | 22.1 |
| 6515 | SONORA 4 | 6562 | FDRAN 4 | 0.0403 | 0.1458 | 0.03994 | 149 | 173 | 149 | 37 |
| 6515 | SONORA 4 | 8259 | CORTHAN4 | 0.0209 | 0.075 | 0.01929 | 147 | 147 | 147 | 18.4 |
| 6535 | BIGLAKE4 | 6536 | BIGLAK24 | 0 | 0.0001 | 0 | 488 | 577 | 488 | 0 |
| 6536 | BIGLAK24 | 6562 | FDRAN 4 | 0.0403 | 0.1458 | 0.03994 | 149 | 173 | 149 | 37 |
| 6579 | FTLCSTR2 | 6582 | MVIEWSW2 | 0.032 | 0.083 | 0.02019 | 117 | 136 | 117 | 19.8 |
| 6582 | MVIEWSW2 | 6583 | MESAVIEW | 0.0065 | 0.0233 | 0.00598 | 147 | 170 | 147 | 5.7 |
| 6584 | INDMESA2 | 6601 | RIOPEC14 | 0.0146 | 0.038 | 0.00924 | 117 | 136 | 117 | 9.1 |
| 6595 | MCCAMYN4 | 6601 | RIOPEC14 | 0.0111 | 0.0395 | 0.01015 | 147 | 170 | 147 | 9.7 |
| 6595 | MCCAMYN4 | 6615 | WTUCRAN4 | 0.0084 | 0.0681 | 0.03735 | 404 | 470 | 404 | 24.6 |
| 6595 | MCCAMYN4 | 60009 | KM ETP4 | 0.0064 | 0.023 | 0.0059 | 147 | 170 | 147 | 5.6 |
| 6601 | RIOPEC14 | 6632 | WDWRDTP4 | 0.0026 | 0.0091 | 0.00235 | 147 | 170 | 147 | 2.2 |
| 6601 | RIOPEC14 | 6635 | KM WTP4 | 0.0101 | 0.0467 | 0.01259 | 176 | 176 | 176 | 11.7 |
| 6601 | RIOPEC14 | 38330 | WDWRDTAP | 0.0022 | 0.0076 | 0.00205 | 139 | 154 | 154 | 1.9 |
| 6615 | WTUCRAN4 | 6635 | KM WTP4 | 0.0097 | 0.0449 | 0.01211 | 176 | 176 | 176 | 11.3 |
| 6627 | COMANCK4 | 6630 | FTSTKPL4 | 0.0225 | 0.08 | 0.02065 | 147 | 170 | 147 | 19.6 |
| 6627 | COMANCK4 | 6632 | WDWRDTP4 | 0.018 | 0.0639 | 0.01649 | 147 | 170 | 147 | 15.7 |
| 6630 | FTSTKPL4 | 6655 | BARRILA4 | 0.029 | 0.1054 | 0.02646 | 144 | 167 | 144 | 25.5 |
| 6630 | FTSTKPL4 | 38340 | AIRPORT4 | 0.0031 | 0.0109 | 0.003 | 139 | 154 | 139 | 2.8 |
| 6632 | WDWRDTP4 | 6633 | WDWRD 4 | 0.0098 | 0.0259 | 0.00705 | 119 | 138 | 119 | 6.5 |
| 6635 | KM WTP4 | 60008 | KM SWP4 | 0.0004 | 0.001 | 0.00029 | 119 | 138 | 119 | 0.3 |
| 6655 | BARRILA4 | 6680 | ALAMITO4 | 0.0766 | 0.2792 | 0.07011 | 144 | 167 | 144 | 67.4 |
| 38310 | 16TH ST | 38330 | WDWRDTAP | 0.036 | 0.1259 | 0.03414 | 154 | 154 | 154 | 31.8 |
| 38310 | 16TH ST | 38340 | AIRPORT4 | 0.0031 | 0.0109 | 0.0344 | 139 | 154 | 139 | 2.8 |
| 38330 | WDWRDTAP | 38331 | WDWRD4 | 0.0114 | 0.0301 | 0.00823 | 119 | 138 | 119 | 7.6 |
| 60004 | KM NEP4 | 60006 | KM SEP4 | 0.0102 | 0.021 | 0.00511 | 101 | 117 | 101 | 5 |
| 60006 | KM SEP4 | 60009 | KM ETP4 | 0.0067 | 0.0233 | 0.00624 | 147 | 170 | 147 | 5.8 |
| 60008 | KM SWP4 | 60021 | KM NWP4 | 0.0069 | 0.0141 | 0.00344 | 101 | 117 | 101 | 3.4 |
|  |  |  |  |  |  | 1.93981 |  |  |  |  |

Appendix E Oncor Switchable Capacitor and Reactor Banks

| Bus # | Name | Vhi | Vlo | Shunt | blocks | block size | blocks | block size | Capacitive Total | Reactive Total |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1010 | Permian 138 | 1.5 | 0.5 | 0 | 2 | 27 |  |  | 54 |  |
| 1015 | Permian 69 | 1.5 | 0.5 | 0 | 2 | 24.3 |  |  | 48.6 |  |
| 1023 | Midland E 138 | 1.5 | 0.5 | 0 | 2 | -25 |  |  |  | -50 |
| 1030 | Morgan 345 | 1.532 | 0.532 | -75 | 1 | -75 |  |  |  | -75 |
| 1032 | Morgan 138 | 1.5 | 0.5 | 0 | 1 | -35 | 3 | -25 |  | -110 |
| 1149 | Dolrhide 138 | 1.5 | 0.5 | 18.4 | 1 | 18.4 |  |  | 18.4 |  |
| 1163 | LaMesa 138 | 1.5 | 0.5 | 18.4 | 1 | 18.4 |  |  | 18.4 |  |
| 1167 | Mustang 138 | 1.5 | 0.5 | 12.6 | 1 | 12.6 |  |  | 12.6 |  |
| 1215 | Pembrook 69 | 1.5 | 0.5 | 0 | 2 | 1.2 |  |  | 2.4 |  |
| 1217 | Glasscock 69 | 1.5 | 0.5 | 0 | 1 | 1.2 |  |  | 1.2 |  |
| 1221 | Tex Harv 69 | 1.5 | 0.5 | 0 | 1 | 9.2 |  |  | 9.2 |  |
| 1227 | Mid Gulf 69 | 1.5 | 0.5 | 0 | 2 | 2.4 |  |  | 4.8 |  |
| 1228 | Midbasin 69 | 1.5 | 0.5 | 0 | 2 | 2.4 |  |  | 4.8 |  |
| 1229 | Stanton 69.6 | 1.5 | 0.5 | 0 | 1 | 9.2 |  |  | 9.2 |  |
| 1237 | S Pegasus 69.6 | 1.5 | 0.5 | 0 | 2 | 1.2 |  |  | 2.4 |  |
| 1256 | Goldsmith 69 | 1.5 | 0.5 | 0 | 1 | 9.2 |  |  | 9.2 |  |
| 1263 | Emma 69 | 1.5 | 0.5 | 0 | 3 | 2.4 |  |  | 7.2 |  |
| 1274 | Fullerton 69.6 | 1.5 | 0.5 | 9 | 2 | 9 |  |  | 18 |  |
| 1310 | Knapp 138 | 1.5 | 0.5 | 0 | 2 | 2.4 |  |  | 4.8 |  |
| 1311 | SA Croc 138 | 1.5 | 0.5 | 0 | 6 | 0.8 |  |  | 4.8 |  |
| 1340 | Eskota 69 | 1.5 | 0.5 | 0 | 2 | 9 |  |  | 18 |  |
| 1347 | IATN/HOW 69.6 | 1.5 | 0.5 | 0 | 2 | 0.3 |  |  | 0.6 |  |
| 1348 | Westbrook 69 | 1.5 | 0.5 | 0 | 2 | 2.4 |  |  | 4.8 |  |
| 1380 | Roscoe 69 | 1.5 | 0.5 | 0 | 1 | 1.2 |  |  | 1.2 |  |
| 1422 | Bowman 345 | 1.5 | 0.5 | 0 | 1 | -25 |  |  |  | -25 |
| 1423 | Bowman 138 | 1.5 | 0.5 | 0 | 1 | -25 |  |  |  | -25 |
| 1430 | Graham 345 | 1.5 | 0.5 | 0 | 2 | -75 |  |  |  | -150 |
| 1431 | Graham 138 | 1.5 | 0.5 | 0 | 1 | -35 | 2 | -25 |  | -85 |
| 1441 | Comanche SS 138 | 1.5 | 0.5 | 0 | 2 | -37.5 |  |  |  | -75 |
| 1467 | Northstr 138 | 1.5 | 0.5 | 1.2 | 1 | 1.2 |  |  | 1.2 |  |
| 1511 | WF Basin 69 | 1.5 | 0.5 | 2.4 | 1 | 2.4 |  |  | 2.4 |  |
| 1518 | Iowapark 69.6 | 1.5 | 0.5 | 9.2 | 1 | 9.2 |  |  | 9.2 |  |
| 1519 | Cryovac 69.6 | 1.5 | 0.5 | 2.4 | 4 | 2.4 |  |  | 9.6 |  |
| 1522 | Navykpoo 69 | 1.5 | 0.5 | 1.8 | 1 | 1.8 |  |  | 1.8 |  |
| 1531 | Seymrbas 69 | 1.5 | 0.5 | 2.4 | 1 | 2.4 |  |  | 2.4 |  |
| 1544 | Henrieta 69 | 1.5 | 0.5 | 1.2 | 3 | 1.2 |  |  | 3.6 |  |
| 1556 | Jack 69 | 1.5 | 0.5 | 7.8 | 2 | 2.1 | 1 | 3.6 | 7.8 |  |
| 1565 | Bridgeport 138 | 1.5 | 0.5 | 7.2 | 1 | 7.2 |  |  | 7.2 |  |
| 1566 | Decatur 138 | 1.5 | 0.5 | 7.2 | 2 | 3.6 |  |  | 7.2 |  |
| 1570 | Rhome 138 | 1.5 | 0.5 | 16.2 | 1 | 16.2 |  |  | 16.2 |  |
| 1588 | Lgnvista 69 | 1.5 | 0.5 | 7.2 | 1 | 7.2 |  |  | 7.2 |  |
| 1602 | Graham 69 | 1.5 | 0.5 | 15.2 | 2 | 7.6 |  |  | 15.2 |  |
| 1632 | Dlnmag 69.6 | 1.5 | 0.5 | 1.2 | 1 | 1.2 |  |  | 1.2 |  |
| 1633 | Deleon 69.6 | 1.5 | 0.5 | 9.2 | 1 | 9.2 |  |  | 9.2 |  |
| 1636 | Dublin 138 | 1.5 | 0.5 | 3.6 | 1 | 3.6 |  |  | 3.6 |  |
| 1641 | Stephenville 138 | 1.5 | 0.5 | 14.4 | 4 | 3.6 |  |  | 14.4 |  |
| 1651 | Comanche 138 | 1.5 | 0.5 | 7.2 | 2 | 3.6 |  |  | 7.2 |  |
| 1655 | Brnwd SS 138 | 1.5 | 0.5 | 18.4 | 2 | 18.4 |  |  | 36.8 |  |
| 1656 | Brnwd S 138 | 1.5 | 0.5 | 10.8 | 3 | 3.6 |  |  | 10.8 |  |
| 1661 | Brnwd 138 | 1.5 | 0.5 | 21.6 | 6 | 2.4 | 2 | 3.6 | 21.6 |  |
| 1670 | Lbrnwd 69 | 1.5 | 0.5 | 3.6 | 1 | 3.6 |  |  | 3.6 |  |
|  |  |  |  |  |  |  |  | Totals | 454 | -595 |
|  |  |  |  |  |  |  |  |  | Capacitive | Reactive |

Appendix F AEP Switchable Capacitor and Reactor Banks

| Bus # | Name | Vhi | Vlo | Shunt | blocks | block size | blocks | block size | blocks | block size | Capacitive Total | Reactive Total |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 6016 | SW Mesa 34.5 | 1.03 | 0.99 | 0 | 1 | 10 |  |  |  |  | 10 |  |
| 6100 | OklaEHV7 345 | 1.05 | 0.95 | 15 | 1 | -39 | 1 | 15.0 |  |  | 15 | -39 |
| 6148 | Spur2 69 | 1.03 | 0.99 | 12 | 1 | 12 |  |  |  |  | 12 |  |
| 6295 | SRC1 tert 13.2 | 1.04 | 0.99 | -36 | 1 | -36 |  |  |  |  |  | -36 |
| 6304 | Clydmag2 69 | 1.03 | 0.99 | 6 | 1 | 6 |  |  |  |  | 6 |  |
| 6305 | Clyde2 69 | 1.03 | 0.99 | 12 | 1 | 12 |  |  |  |  | 12 |  |
| 6423 | Cedarhill2 69 | 1.03 | 0.99 | 12 | 1 | 12 |  |  |  |  | 12 |  |
| 6442 | SA Red Creek4 138 | 1.04 | 0.99 | 50 | 1 | 25.2 | 1 | 25.2 |  |  | 50.4 |  |
| 6455 | SA South2 69 | 1.03 | 0.99 | 2.4 | 1 | 2.4 |  |  |  |  | 2.4 |  |
| 6462 | SA North2 69 | 1.03 | 0.99 | 21.6 | 1 | 21.6 | 1 | 2.4 |  |  | 24 |  |
| 6468 | SA Chwst2 69 | 1.03 | 0.99 | 0 | 1 | 21.6 |  |  |  |  | 21.6 |  |
| 6498 | Live Oak2 69 | 1.03 | 0.99 | 0 | 1 | 12 |  |  |  |  | 12 |  |
| 6510 | Snrcity2 69 | 1.03 | 0.99 | 0 | 1 | 12 |  |  |  |  | 12 |  |
| 6545 | Powlfld2 69 | 1.03 | 0.99 | 0 | 1 | 6.6 | 1 | 6.6 |  |  | 13.2 |  |
| 6549 | Midwyln2 69 | 1.03 | 0.99 | 1.8 | 1 | 1.8 |  |  |  |  | 1.8 |  |
| 6575 | Iraan2 69 | 1.03 | 0.97 | 6 | 1 | 6 |  |  |  |  | 6 |  |
| 6580 | Airpdts2 69 | 1.03 | 0.98 | 6.6 | 1 | 6.6 |  |  |  |  | 6.6 |  |
| 6601 | Rio Pec14 138 | 1.04 | 0.99 | -40 | 2 | -20 | 1 | 25 |  |  | 25 | -40 |
| 6608 | Crangu12 69 | 1.03 | 0.99 | 0 | 1 | 1.5 |  |  |  |  | 1.5 |  |
| 6684 | Presidio2 69 | 1.03 | 0.99 | 2 | 1 | 2 |  |  |  |  | 2 |  |
| 6769 | Src2 tert 13.2 | 1.04 | 0.99 | -36 | 1 | -36 |  |  |  |  |  | -36 |
| 6780 | Ok1 tert 13.2 | 1.04 | 0.99 | 0 | 1 | -36 |  |  |  |  |  | -36 |
| 6789 | Amcw tert 13.2 | 1.03 | 0.99 | 0 | 1 | -36 |  |  |  |  |  | -36 |
| 60003 | KM NEP 34.5 | 1.04 | 0.98 | 0 | 1 | 9 | 1 | 9 |  |  | 18 |  |
| 60005 | KM SEP 34.5 | 1.04 | 0.98 | 0 | 1 | 7 |  |  |  |  | 7 |  |
| 60007 | KM SWP 34.5 | 1.04 | 0.98 | 0 | 1 | 9 | 1 | 9 |  |  | 18 |  |
| 60017 | Orion NWP1 34.5 | 1.03 | 0.99 | 0 | 1 | 6 | 1 | 6 | 1 | 6 | 18 |  |
| 60019 | KM NWP 34.5 | 1.04 | 0.98 | 0 | 1 | 9 | 1 | 9 |  |  | 18 |  |
|  |  |  |  |  |  |  |  |  | Totals |  | 284.5 | -223 |
|  |  |  |  |  |  |  |  |  |  |  | Capacitive | Reactive |

Appendix G TXU Energy Generator Reactive Limits

| BUS# | NAME | BSKV | ID | ST | PGEN | QGEN | QMAX | QMIN | PMAX | PMIN |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1002 | PBCT A G | 13.8 | A | 0 | 0 | 0 | 52 | -23 | 70 | 70 |
| 1003 | PBCT B G | 13.8 | B | 0 | 0 | 0 | 52 | -23 | 70 | 70 |
| 1004 | PBCT C G | 13.8 | C | 0 | 0 | 0 | 52 | -23 | 70 | 70 |
| 1005 | PBCT D G | 13.8 | D | 0 | 0 | 0 | 52 | -23 | 70 | 70 |
| 1006 | PBCT E G | 13.8 | E | 0 | 0 | 0 | 52 | -23 | 70 | 70 |
| 1007 | PB5 G | 13.8 | 5 | 0 | 0 | 0 | 58 | -25 | 115 | 40 |
| 1008 | PB6 G | 18 | 6 | 0 | 0 | 0 | 213 | -30 | 540 | 130 |
| 1031 | MRGN 6 G | 22 | 6 | 0 | 0 | 0 | 235 | -90 | 511 | 250 |
| 1035 | MORGAN2G | 13.2 | 2 | 0 | 0 | 0 | 8 | -2 | 22 | 7 |
| 1036 | MORGAN4G | 13.8 | 4 | 0 | 0 | 0 | 45 | -20 | 70 | 20 |
| 1037 | MORGAN5G | 20 | 5 | 0 | 0 | 0 | 79 | -36 | 175 | 40 |
| 1038 | MORGAN3G | 13.2 | 3 | 0 | 0 | 0 | 28 | -20 | 44 | 14 |
| 1039 | MRGN A G | 13.8 | A | 0 | 0 | 0 | 43 | -23 | 70 | 70 |
| 1040 | MRGN B G | 13.8 | B | 0 | 0 | 0 | 43 | -23 | 70 | 70 |
| 1041 | MRGN C G | 13.8 | C | 0 | 0 | 0 | 43 | -23 | 70 | 70 |
| 1042 | MRGN D G | 13.8 | D | 0 | 0 | 0 | 43 | -23 | 70 | 70 |
| 1043 | MRGN E G | 13.8 | E | 0 | 0 | 0 | 43 | -23 | 70 | 70 |
| 1044 | MRGN F G | 13.8 | F | 0 | 0 | 0 | 43 | -23 | 70 | 70 |
| 1045 | CALENG1G | 13.8 | 1 | 1 | 52.5 | 9.3 | 43 | -23 | 70 | 27 |
| 1046 | CALENG2G | 13.8 | 2 | 1 | 52.5 | 9.3 | 46 | -26 | 70 | 27 |
| 1047 | CALENG3G | 13.8 | 3 | 1 | 45 | 8.0 | 55 | -36 | 60 | 27 |
| 1343 | TRENTIPP | 138 | 1 | 1 | 30 | -2.8 | 44 | -44 | 150 | 10 |
| 1350 | NWPWR G1 | 13.8 | 1 | 1 | 7 | -4 | 8 | -4 | 35 | 4 |
| 1416 | SWTWTR1G | 13.8 | 1 | 1 | 0 | 0 | 16 | -10 | 35 | 18 |
| 1417 | SWTWTR2G | 13.8 | 2 | 1 | 0 | 0 | 39 | -20 | 75 | 36 |
| 1418 | SWTWTR3G | 13.8 | 3 | 1 | 0 | 0 | 39 | -20 | 75 | 36 |
| 1419 | SWTWTR4G | 13.8 | 4 | 1 | 0 | 0 | 58 | -20 | 85 | 36 |
| 1432 | GRAM 2 G | 22 | 2 | 0 | 0 | 0 | 162 | -75 | 390 | 90 |
| 1433 | GRAM 1 G | 20 | 1 | 0 | 0 | 0 | 145 | -28 | 240 | 60 |
| 11020 | TIEHV SG | 18 | 1 | 0 | 0 | 0 | 127 | -67 | 180 | 63 |
| 11021 | TIEHV CG | 18 | 1 | 0 | 0 | 0 | 106 | -56 | 160 | 103 |
| 11022 | TIEHV CG | 18 | 1 | 0 | 0 | 0 | 106 | -56 | 160 | 103 |
| 11023 | TIEHV CG | 18 | 1 | 0 | 0 | 0 | 106 | -56 | 160 | 103 |
| 11024 | TIEHV CG | 18 | 1 | 0 | 0 | 0 | 106 | -56 | 160 | 103 |
| 11025 | TIEHV SG | 18 | 1 | 0 | 0 | 0 | 127 | -67 | 180 | 63 |
|  | Totals |  |  |  |  |  | 2517 | -1140 |  |  |
|  |  |  |  |  |  |  | Qmax | Qmin |  |  |

Appendix H AEP Generator Reactive Limits

| BUS# | NAME | BSKV | ID | ST | PGEN | QGEN | QMAX | QMIN | PMAX | PMIN |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 6016 | SWMESA | 34.5 | 1 | 1 | 15 | 0 | 0 | 0 | 75 | 0 |
| 6061 | VERNPLT2 | 69 | 1 | 0 | 0 | 0 | 4 | 0 | 9 | 1 |
| 6282 | ABILPLT2 | 69 | 4 | 0 | 0 | 0 | 12 | -4 | 18 | 10 |
| 6628 | FTSTKPL2 | 69 | 1 | 0 | 0 | 0 | 3 | 0 | 5 | 0 |
| 6677 | VALTNTP2 | 69 | 1 | 1 | 0.2 | 0 | 0 | 0 | 5.5 | 0 |
| 6685 | PRSIDIO | 12.5 | 1 | 0 | 0 | 0 | 1 | -1 | 2 | 2 |
| 6694 | WFORD1G | 12 | 1 | 0 | 0 | 0 | 1 | -1 | 5 | 0 |
| 6750 | LKPAUL1G | 13.8 | 1 | 0 | 0 | 0 | 8 | -3 | 12 | 8 |
| 6751 | LKPAUL2G | 13.8 | 2 | 0 | 0 | 0 | 13 | -5 | 23 | 10 |
| 6752 | OKLAUN1G | 24 | 1 | 1 | 698 | 49.4 | 400 | -280 | 698 | 175 |
| 6753 | PTCREK1G | 13.8 | 1 | 0 | 0 | 0 | 16 | -4 | 32 | 10 |
| 6754 | PTCREK2G | 13.8 | 2 | 0 | 0 | 0 | 16 | -4 | 33 | 10 |
| 6755 | PTCREK3G | 13.8 | 3 | 0 | 0 | 0 | 25 | -8 | 54 | 16 |
| 6756 | PTCREK4G | 14.4 | 4 | 0 | 0 | 0 | 40 | -17 | 118 | 25 |
| 6757 | PHANTM1G | 14.4 | 1 | 0 | 0 | 0 | 75 | -25 | 158 | 35 |
| 6758 | PHANTM2G | 20 | 2 | 0 | 0 | 0 | 100 | -35 | 204 | 45 |
| 6759 | OAKCK 1G | 13.8 | 1 | 0 | 0 | 0 | 39 | -14 | 85 | 20 |
| 6762 | SAPS 1G | 14.4 | 1 | 0 | 0 | 0 | 18 | -14 | 30 | 21 |
| 6763 | SAPS 2G | 14.4 | 2 | 0 | 0 | 0 | 38 | -35 | 102 | 30 |
| 6764 | RIOPEC4G | 13.2 | 4 | 0 | 0 | 0 | 3 | 0 | 4 | 0 |
| 6765 | RIOPEC5G | 13.8 | 5 | 0 | 0 | 0 | 23 | -9 | 34 | 8 |
| 6766 | RIOPEC6G | 14.4 | 6 | 0 | 0 | 0 | 30 | -20 | 98 | 20 |
| 38332 | WDWRDU2 | 34.5 | 1 | 1 | 16 | 0 | 0 | 0 | 80 | 0 |
| 60000 | INDM2 PP | 34.5 | 1 | 1 | 16 | 0 | 0 | 0 | 80 | 0 |
| 60003 | KM NEP | 34.5 | 1 | 1 | 16 | 0 | 0 | 0 | 80 | 0 |
| 60005 | KM SEP | 34.5 | 1 | 1 | 8 | 0 | 0 | 0 | 40 | 0 |
| 60007 | KM SWP | 34.5 | 1 | 1 | 16 | 0 | 0 | 0 | 80 | 0 |
| 60016 | WDWDU1 | 34.5 | 1 | 1 | 16 | 0 | 0 | 0 | 80 | 0 |
| 60017 | ORNNWP1 | 34.5 | 1 | 1 | 16.4 | 0 | 0 | 0 | 82.5 | 0 |
| 60018 | INDM1 PP | 34.5 | 1 | 1 | 16 | 0 | 0 | 0 | 80 | 0 |
| 60019 | KM NWP | 34.5 | 1 | 1 | 16 | 0 | 0 | 0 | 80 | 0 |
| 60023 | NOLK1WP | 34.5 | 1 | 1 | 0 | 0 | 0 | 0 | 9999 | -9999 |
|  |  |  |  |  |  |  | 865 | -479 |  |  |

Appendix I 2003 Fall Off-Peak Base Case Generation Dispatch

| BUS# | NAME | BSKV | COD | MCNS | PGEN | QGEN | QMAX | QMIN |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1002 | PBCT A G | 13.8 | -2 | 1 | 0 | 0 | 0 | 0 |
| 1003 | PBCT B G | 13.8 | -2 | 1 | 0 | 0 | 0 | 0 |
| 1004 | PBCT C G | 13.8 | -2 | 1 | 0 | 0 | 0 | 0 |
| 1005 | PBCT D G | 13.8 | -2 | 1 | 0 | 0 | 0 | 0 |
| 1006 | PBCT E G | 13.8 | -2 | 1 | 0 | 0 | 0 | 0 |
| 1007 | PB5 G | 13.8 | -2 | 1 | 0 | 0 | 0 | 0 |
| 1008 | PB6 G | 18 | -2 | 1 | 0 | 0 | 0 | 0 |
| 1031 | MRGN 6 G | 22 | -2 | 1 | 0 | 0 | 0 | 0 |
| 1035 | MORGAN2G | 13.2 | -2 | 1 | 0 | 0 | 0 | 0 |
| 1036 | MORGAN4G | 13.8 | -2 | 1 | 0 | 0 | 0 | 0 |
| 1037 | MORGAN5G | 20 | -2 | 1 | 0 | 0 | 0 | 0 |
| 1038 | MORGAN3G | 13.2 | -2 | 1 | 0 | 0 | 0 | 0 |
| 1039 | MRGN A G | 13.8 | -2 | 1 | 0 | 0 | 0 | 0 |
| 1040 | MRGN B G | 13.8 | -2 | 1 | 0 | 0 | 0 | 0 |
| 1041 | MRGN C G | 13.8 | -2 | 1 | 0 | 0 | 0 | 0 |
| 1042 | MRGN D G | 13.8 | -2 | 1 | 0 | 0 | 0 | 0 |
| 1043 | MRGN E G | 13.8 | -2 | 1 | 0 | 0 | 0 | 0 |
| 1044 | MRGN F G | 13.8 | -2 | 1 | 0 | 0 | 0 | 0 |
| 1045 | CALENG1G | 13.8 | 2 | 1 | 52.5 | 10.5 | 43 | -23 |
| 1046 | CALENG2G | 13.8 | 2 | 1 | 52.5 | 10.5 | 46 | -26 |
| 1047 | CALENG3G | 13.8 | 2 | 1 | 45 | 9 | 55 | -36 |
| 1050 | ENRONIPP | 345 | -2 | 1 | 0 | 0 | 0 | 0 |
| 1146 | YORK IPP | 138 | -2 | 1 | 0 | 0 | 0 | 0 |
| 1343 | TRENTIPP | 138 | 2 | 1 | 30 | -1.6 | 44 | -44 |
| 1350 | NWPWR G1 | 13.8 | -2 | 1 | 7 | -4 | 8 | -4 |
| 1416 | SWTWTR1G | 13.8 | -2 | 1 | 0 | 0 | 0 | 0 |
| 1417 | SWTWTR2G | 13.8 | -2 | 1 | 0 | 0 | 0 | 0 |
| 1418 | SWTWTR3G | 13.8 | -2 | 1 | 0 | 0 | 0 | 0 |
| 1419 | SWTWTR4G | 13.8 | -2 | 1 | 0 | 0 | 0 | 0 |
| 1432 | GRAM 2 G | 22 | -2 | 1 | 0 | 0 | 0 | 0 |
| 1433 | GRAM 1 G | 20 | -2 | 1 | 0 | 0 | 0 | 0 |
| 1898 | CMPK 1 G | 22 | 2 | 1 | 1150 | 117.7 | 359 | -228 |
| 1899 | CMPK 2 G | 22 | 2 | 1 | 1150 | 117.7 | 357 | -226 |
| 6016 | SWMESA | 34.5 | -2 | 1 | 15 | 0 | 0 | 0 |
| 6061 | VERNPLT2 | 69 | -2 | 1 | 0 | 0 | 0 | 0 |
| 6096 | NORTHDC7 | 345 | -2 | 1 | 0 | 0 | 0 | 0 |
| 6282 | ABILPLT2 | 69 | -2 | 1 | 0 | 0 | 0 | 0 |
| 6628 | FTSTKPL2 | 69 | -2 | 1 | 0 | 0 | 0 | 0 |
| 6677 | VALTNTP2 | 69 | -2 | 1 | 0.2 | 0 | 0 | 0 |
| 6685 | PRSIDIO | 12.5 | -2 | 1 | 0 | 0 | 0 | 0 |
| 6694 | WFORD1G | 12 | -2 | 1 | 0 | 0 | 0 | 0 |
| 6750 | LKPAUL1G | 13.8 | 4 | 1 | 0 | 0 | 0 | 0 |
| 6751 | LKPAUL2G | 13.8 | 4 | 1 | 0 | 0 | 0 | 0 |
| 6752 | OKLAUN1G | 24 | 2 | 1 | 698 | 50.9 | 400 | -280 |
| 6753 | PTCREK1G | 13.8 | 4 | 1 | 0 | 0 | 0 | 0 |
| 6754 | PTCREK2G | 13.8 | -2 | 1 | 0 | 0 | 0 | 0 |
| 6755 | PTCREK3G | 13.8 | 4 | 1 | 0 | 0 | 0 | 0 |
| 6756 | PTCREK4G | 14.4 | 4 | 1 | 0 | 0 | 0 | 0 |
| 6757 | PHANTM1G | 14.4 | -2 | 1 | 0 | 0 | 0 | 0 |
| 6758 | PHANTM2G | 20 | -2 | 1 | 0 | 0 | 0 | 0 |
| 6759 | OAKCK 1G | 13.8 | 4 | 1 | 0 | 0 | 0 | 0 |
| 6762 | SAPS 1G | 14.4 | -2 | 1 | 0 | 0 | 0 | 0 |
| 6763 | SAPS 2G | 14.4 | -2 | 1 | 0 | 0 | 0 | 0 |
| 6764 | RIOPEC4G | 13.2 | -2 | 1 | 0 | 0 | 0 | 0 |
| 6765 | RIOPEC5G | 13.8 | -2 | 1 | 0 | 0 | 0 | 0 |
| 6766 | RIOPEC6G | 14.4 | -2 | 1 | 0 | 0 | 0 | 0 |
| 7038 | TWPP G1 | 34.5 | 2 | 2 | 14.1 | -8 | 14 | -14 |
| 11020 | TIEHV SG | 18 | -2 | 1 | 0 | 0 | 0 | 0 |
| 11021 | TIEHV CG | 18 | -2 | 1 | 0 | 0 | 0 | 0 |
| 11022 | TIEHV CG | 18 | -2 | 1 | 0 | 0 | 0 | 0 |
| 11023 | TIEHV CG | 18 | -2 | 1 | 0 | 0 | 0 | 0 |
| 11024 | TIEHV CG | 18 | -2 | 1 | 0 | 0 | 0 | 0 |
| 11025 | TIEHV SG | 18 | -2 | 1 | 0 | 0 | 0 | 0 |
| 38332 | WDWRDU2 | 34.5 | -2 | 1 | 16 | 0 | 0 | 0 |
| 60000 | INDM2 PP | 34.5 | -2 | 1 | 16 | 0 | 0 | 0 |
| 60003 | KM NEP | 34.5 | -2 | 1 | 16 | 0 | 0 | 0 |
| 60005 | KM SEP | 34.5 | -2 | 1 | 8 | 0 | 0 | 0 |
| 60007 | KM SWP | 34.5 | -2 | 1 | 16 | 0 | 0 | 0 |
| 60016 | WDWDU1 | 34.5 | -2 | 1 | 16 | 0 | 0 | 0 |
| 60017 | ORNNWP1 | 34.5 | -2 | 1 | 16.4 | 0 | 0 | 0 |
| 60018 | INDM1 PP | 34.5 | -2 | 1 | 16 | 0 | 0 | 0 |
| 60019 | KM NWP | 34.5 | -2 | 1 | 16 | 0 | 0 | 0 |
| 60023 | NOLK1WP | 34.5 | 1 | 1 | 0 | 0 | 0 | 0 |
|  |  |  |  |  | 3351 |  |  |  |
| Note: the spring off-peak dispatch matches this except that |  |  |  |  |  |  |  |  |
| Morgan Creek 6 is at Pgen = 250 MW. |  |  |  |  |  |  |  |  |
| Blue color indicates a windpower plant. |  |  |  |  |  |  |  |  |

Appendix J Fall Off-Peak Voltages for Varying Windpower and Oncor Load Power-Factors

| Bus per unit Voltages, Fall Off-Peak, Varying Wind |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| and Oncor load power factor |  |  |  |  |  |  |
| Number | Bus name, nominal kV | Oncor load pf | wind = 20% nameplate | wind = 40% nameplate | wind = 60% nameplate | wind = 80% nameplate |
| 6009 | Twin Buttes 345 | 0.964 | 1.045 | 1.052 | 1.052 | 1.049 |
|  |  | 0.97 | 1.049 | 1.056 | 1.057 | 1.053 |
|  |  | 0.975 | 1.052 | 1.06 | 1.06 | 1.056 |
|  |  | 0.98 | 1.056 | 1.064 | 1.065 | 1.061 |
|  |  | 0.985 | 1.06 | 1.069 | 1.069 | 1.062 |
|  |  | 0.99 | 1.065 | 1.074 | 1.075 | 1.067 |
| 1420 | Sweetwater 345 | 0.964 | 1.042 | 1.048 | 1.048 | 1.044 |
|  |  | 0.97 | 1.046 | 1.052 | 1.052 | 1.048 |
|  |  | 0.975 | 1.05 | 1.056 | 1.057 | 1.053 |
|  |  | 0.98 | 1.054 | 1.061 | 1.062 | 1.058 |
|  |  | 0.985 | 1.06 | 1.066 | 1.067 | 1.06 |
|  |  | 0.99 | 1.066 | 1.073 | 1.074 | 1.066 |
| 6444 | Red Creek 345 | 0.964 | 1.043 | 1.051 | 1.051 | 1.048 |
|  |  | 0.97 | 1.047 | 1.055 | 1.055 | 1.051 |
|  |  | 0.975 | 1.05 | 1.057 | 1.058 | 1.055 |
|  |  | 0.98 | 1.054 | 1.061 | 1.063 | 1.059 |
|  |  | 0.985 | 1.057 | 1.066 | 1.067 | 1.06 |
|  |  | 0.99 | 1.062 | 1.071 | 1.072 | 1.064 |
| 1050 | Enron IPP 345 | 0.964 | 1.04 | 1.047 | 1.047 | 1.043 |
|  |  | 0.97 | 1.044 | 1.05 | 1.051 | 1.047 |
|  |  | 0.975 | 1.048 | 1.054 | 1.055 | 1.051 |
|  |  | 0.98 | 1.052 | 1.059 | 1.059 | 1.056 |
|  |  | 0.985 | 1.057 | 1.063 | 1.064 | 1.057 |
|  |  | 0.99 | 1.062 | 1.069 | 1.07 | 1.063 |
| 1030 | Morgan Creek 345 | 0.964 | 1.037 | 1.044 | 1.043 | 1.037 |
|  |  | 0.97 | 1.041 | 1.049 | 1.047 | 1.042 |
|  |  | 0.975 | 1.046 | 1.053 | 1.052 | 1.047 |
|  |  | 0.98 | 1.051 | 1.058 | 1.058 | 1.053 |
|  |  | 0.985 | 1.057 | 1.064 | 1.064 | 1.054 |
|  |  | 0.99 | 1.063 | 1.071 | 1.071 | 1.061 |
| 1020 | Odessa EHV 345 | 0.964 | 1.026 | 1.033 | 1.028 | 1.016 |
|  |  | 0.97 | 1.033 | 1.04 | 1.035 | 1.024 |
|  |  | 0.975 | 1.04 | 1.047 | 1.043 | 1.032 |
|  |  | 0.98 | 1.047 | 1.055 | 1.051 | 1.04 |
|  |  | 0.985 | 1.056 | 1.063 | 1.06 | 1.041 |
|  |  | 0.99 | 1.066 | 1.073 | 1.07 | 1.052 |
| 6230 | Mulberry 345 | 0.964 | 1.04 | 1.046 | 1.046 | 1.044 |
|  |  | 0.97 | 1.043 | 1.05 | 1.049 | 1.047 |
|  |  | 0.975 | 1.046 | 1.052 | 1.053 | 1.051 |
|  |  | 0.98 | 1.049 | 1.055 | 1.056 | 1.054 |
|  |  | 0.985 | 1.053 | 1.059 | 1.06 | 1.055 |
|  |  | 0.99 | 1.057 | 1.064 | 1.065 | 1.06 |
| 1025 | FS Cogen 345 | 0.964 | 1.034 | 1.039 | 1.037 | 1.031 |
|  |  | 0.97 | 1.038 | 1.043 | 1.041 | 1.036 |
|  |  | 0.975 | 1.041 | 1.047 | 1.046 | 1.041 |
|  |  | 0.98 | 1.045 | 1.051 | 1.05 | 1.045 |
|  |  | 0.985 | 1.051 | 1.056 | 1.055 | 1.046 |
|  |  | 0.99 | 1.056 | 1.062 | 1.061 | 1.052 |
| 1018 | Moss 345 | 0.964 | 1.016 | 1.022 | 1.017 | 1.004 |
|  |  | 0.97 | 1.023 | 1.03 | 1.024 | 1.012 |
|  |  | 0.975 | 1.03 | 1.037 | 1.033 | 1.021 |
|  |  | 0.98 | 1.037 | 1.045 | 1.042 | 1.03 |
|  |  | 0.985 | 1.046 | 1.054 | 1.051 | 1.032 |
|  |  | 0.99 | 1.056 | 1.064 | 1.06 | 1.042 |
| 1021 | Midland 345 | 0.964 | 1.015 | 1.021 | 1.017 | 1.006 |
|  |  | 0.97 | 1.02 | 1.028 | 1.023 | 1.013 |
|  |  | 0.975 | 1.027 | 1.034 | 1.031 | 1.022 |
|  |  | 0.98 | 1.033 | 1.042 | 1.039 | 1.029 |
|  |  | 0.985 | 1.041 | 1.048 | 1.047 | 1.031 |
|  |  | 0.99 | 1.051 | 1.058 | 1.055 | 1.04 |
| 6021 | Indian Mesa 138 | 0.964 | 1.035 | 1.054 | 1.046 | 1.043 |
|  |  | 0.97 | 1.041 | 1.056 | 1.054 | 1.048 |
|  |  | 0.975 | 1.043 | 1.058 | 1.055 | 1.05 |
|  |  | 0.98 | 1.045 | 1.055 | 1.056 | 1.052 |
|  |  | 0.985 | 1.044 | 1.058 | 1.054 | 1.027 |
|  |  | 0.99 | 1.043 | 1.057 | 1.055 | 1.033 |
| 6022 | IndM1 T4 138 | 0.964 | 1.035 | 1.054 | 1.046 | 1.043 |
|  |  | 0.97 | 1.041 | 1.056 | 1.054 | 1.048 |
|  |  | 0.975 | 1.043 | 1.058 | 1.055 | 1.05 |
|  |  | 0.98 | 1.045 | 1.055 | 1.056 | 1.051 |
|  |  | 0.985 | 1.044 | 1.058 | 1.054 | 1.027 |
|  |  | 0.99 | 1.043 | 1.057 | 1.055 | 1.033 |
| 6582 | MesaView2 138 | 0.964 | 1.034 | 1.053 | 1.045 | 1.041 |
|  |  | 0.97 | 1.04 | 1.055 | 1.053 | 1.046 |
|  |  | 0.975 | 1.043 | 1.057 | 1.054 | 1.048 |
|  |  | 0.98 | 1.044 | 1.054 | 1.055 | 1.049 |
|  |  | 0.985 | 1.043 | 1.057 | 1.053 | 1.025 |
|  |  | 0.99 | 1.043 | 1.056 | 1.054 | 1.031 |
| 6583 | Mesa View 138 | 0.964 | 1.034 | 1.053 | 1.045 | 1.041 |
|  |  | 0.97 | 1.04 | 1.055 | 1.053 | 1.046 |
|  |  | 0.975 | 1.043 | 1.057 | 1.054 | 1.048 |
|  |  | 0.98 | 1.044 | 1.054 | 1.055 | 1.049 |
|  |  | 0.985 | 1.043 | 1.057 | 1.053 | 1.025 |
|  |  | 0.99 | 1.043 | 1.056 | 1.054 | 1.031 |
| 6019 | Orion 138 | 0.964 | 1.033 | 1.051 | 1.043 | 1.04 |
|  |  | 0.97 | 1.04 | 1.053 | 1.051 | 1.045 |
|  |  | 0.975 | 1.042 | 1.055 | 1.052 | 1.046 |
|  |  | 0.98 | 1.043 | 1.053 | 1.053 | 1.048 |
|  |  | 0.985 | 1.042 | 1.056 | 1.051 | 1.024 |
|  |  | 0.99 | 1.042 | 1.055 | 1.052 | 1.03 |
| 6578 | Ft Lancaster 69 | 0.964 | 1.031 | 1.051 | 1.046 | 1.043 |
|  |  | 0.97 | 1.036 | 1.053 | 1.053 | 1.047 |
|  |  | 0.975 | 1.038 | 1.055 | 1.054 | 1.049 |
|  |  | 0.98 | 1.039 | 1.052 | 1.055 | 1.051 |
|  |  | 0.985 | 1.039 | 1.055 | 1.054 | 1.029 |
|  |  | 0.99 | 1.038 | 1.054 | 1.054 | 1.035 |
| 6579 | Ft Lancster 138 | 0.964 | 1.033 | 1.051 | 1.042 | 1.036 |
|  |  | 0.97 | 1.039 | 1.052 | 1.049 | 1.041 |
|  |  | 0.975 | 1.041 | 1.054 | 1.05 | 1.042 |
|  |  | 0.98 | 1.041 | 1.052 | 1.051 | 1.044 |
|  |  | 0.985 | 1.041 | 1.054 | 1.049 | 1.021 |
|  |  | 0.99 | 1.041 | 1.053 | 1.05 | 1.027 |
| 60004 | King NE 138 | 0.964 | 1.033 | 1.049 | 1.038 | 1.031 |
|  |  | 0.97 | 1.039 | 1.051 | 1.046 | 1.036 |
|  |  | 0.975 | 1.042 | 1.053 | 1.047 | 1.037 |
|  |  | 0.98 | 1.043 | 1.044 | 1.048 | 1.039 |
|  |  | 0.985 | 1.042 | 1.053 | 1.046 | 1.017 |
|  |  | 0.99 | 1.042 | 1.052 | 1.047 | 1.023 |
| 38380 | Puckittap 69 | 0.964 | 1.037 | 1.048 | 1.033 | 1.024 |
|  |  | 0.97 | 1.044 | 1.042 | 1.042 | 1.029 |
|  |  | 0.975 | 1.046 | 1.052 | 1.042 | 1.03 |
|  |  | 0.98 | 1.048 | 1.045 | 1.044 | 1.032 |
|  |  | 0.985 | 1.047 | 1.052 | 1.042 | 1.01 |
|  |  | 0.99 | 1.046 | 1.052 | 1.043 | 1.015 |
| 38390 | Armadillo 69 | 0.964 | 1.037 | 1.047 | 1.033 | 1.023 |
|  |  | 0.97 | 1.044 | 1.042 | 1.042 | 1.029 |
|  |  | 0.975 | 1.046 | 1.052 | 1.042 | 1.03 |
|  |  | 0.98 | 1.048 | 1.045 | 1.044 | 1.032 |
|  |  | 0.985 | 1.047 | 1.052 | 1.042 | 1.01 |
|  |  | 0.99 | 1.046 | 1.052 | 1.043 | 1.015 |
| 6584 | IndianMesa2 138 | 0.964 | 1.031 | 1.047 | 1.037 | 1.033 |
|  |  | 0.97 | 1.037 | 1.041 | 1.045 | 1.037 |
|  |  | 0.975 | 1.039 | 1.051 | 1.046 | 1.039 |
|  |  | 0.98 | 1.041 | 1.042 | 1.047 | 1.041 |
|  |  | 0.985 | 1.04 | 1.051 | 1.045 | 1.016 |
|  |  | 0.99 | 1.039 | 1.05 | 1.046 | 1.022 |
| 6500 | Live Oak 138 | 0.964 | 1.043 | 1.049 | 1.045 | 1.036 |
|  |  | 0.97 | 1.043 | 1.03 | 1.046 | 1.039 |
|  |  | 0.975 | 1.045 | 1.05 | 1.048 | 1.042 |
|  |  | 0.98 | 1.044 | 1.032 | 1.047 | 1.041 |
|  |  | 0.985 | 1.046 | 1.036 | 1.046 | 1.032 |
|  |  | 0.99 | 1.045 | 1.038 | 1.045 | 1.036 |
| 6577 | Sheffield 69 | 0.964 | 1.026 | 1.046 | 1.04 | 1.036 |
|  |  | 0.97 | 1.032 | 1.039 | 1.047 | 1.041 |
|  |  | 0.975 | 1.034 | 1.05 | 1.048 | 1.042 |
|  |  | 0.98 | 1.035 | 1.041 | 1.05 | 1.044 |
|  |  | 0.985 | 1.035 | 1.047 | 1.048 | 1.022 |
|  |  | 0.99 | 1.034 | 1.048 | 1.049 | 1.028 |
| 6630 | Ft Stockton 138 | 0.964 | 1.035 | 1.045 | 1.031 | 1.021 |
|  |  | 0.97 | 1.042 | 1.04 | 1.04 | 1.027 |
|  |  | 0.975 | 1.045 | 1.041 | 1.04 | 1.028 |
|  |  | 0.98 | 1.047 | 1.043 | 1.042 | 1.03 |
|  |  | 0.985 | 1.045 | 1.05 | 1.04 | 1.008 |
|  |  | 0.99 | 1.045 | 1.05 | 1.041 | 1.014 |
| 38320 | 16th St 138 | 0.964 | 1.035 | 1.045 | 1.031 | 1.022 |
|  |  | 0.97 | 1.042 | 1.04 | 1.04 | 1.027 |
|  |  | 0.975 | 1.044 | 1.041 | 1.04 | 1.028 |
|  |  | 0.98 | 1.046 | 1.043 | 1.042 | 1.03 |
|  |  | 0.985 | 1.045 | 1.05 | 1.04 | 1.008 |
|  |  | 0.99 | 1.044 | 1.05 | 1.041 | 1.014 |
| 38340 | Airport 138 | 0.964 | 1.035 | 1.045 | 1.031 | 1.021 |
|  |  | 0.97 | 1.042 | 1.04 | 1.04 | 1.027 |
|  |  | 0.975 | 1.045 | 1.041 | 1.04 | 1.028 |
|  |  | 0.98 | 1.046 | 1.043 | 1.042 | 1.03 |
|  |  | 0.985 | 1.045 | 1.05 | 1.04 | 1.008 |
|  |  | 0.99 | 1.045 | 1.05 | 1.041 | 1.014 |

Appendix K Fall Off-Peak Voltages for Varying Windpower and Oncor Load Power-Factors for Existing Windpower Modeled with 98% Reactive Power Capability

| Bus per unit Voltages, Fall Off-Peak, Varying Wind |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| and Oncor load power factor |  |  |  | Wind pf = .98 |  |  |
| Number | Bus name, nominal kV | Oncor load pf | wind = 20% nameplate | wind = 40% nameplate | wind = 60% nameplate | wind = 80% nameplate |
| 6009 | Twin Buttes 345 | 0.964 | 1.043 | 1.048 | 1.049 | 1.047 |
|  |  | 0.97 | 1.045 | 1.051 | 1.052 | 1.049 |
|  |  | 0.975 | 1.048 | 1.053 | 1.055 | 1.052 |
|  |  | 0.98 | 1.052 | 1.057 | 1.059 | 1.056 |
|  |  | 0.985 | 1.057 | 1.061 | 1.063 | 1.060 |
|  |  | 0.99 | 1.061 | 1.067 | 1.068 | 1.065 |
| 1420 | Sweetwater 345 | 0.964 | 1.040 | 1.045 | 1.045 | 1.042 |
|  |  | 0.97 | 1.043 | 1.048 | 1.049 | 1.045 |
|  |  | 0.975 | 1.047 | 1.051 | 1.052 | 1.050 |
|  |  | 0.98 | 1.051 | 1.055 | 1.057 | 1.054 |
|  |  | 0.985 | 1.057 | 1.061 | 1.062 | 1.060 |
|  |  | 0.99 | 1.063 | 1.067 | 1.069 | 1.065 |
| 6444 | Red Creek 345 | 0.964 | 1.041 | 1.047 | 1.048 | 1.046 |
|  |  | 0.97 | 1.043 | 1.049 | 1.050 | 1.048 |
|  |  | 0.975 | 1.046 | 1.051 | 1.053 | 1.051 |
|  |  | 0.98 | 1.050 | 1.055 | 1.057 | 1.054 |
|  |  | 0.985 | 1.054 | 1.059 | 1.060 | 1.058 |
|  |  | 0.99 | 1.058 | 1.064 | 1.065 | 1.062 |
| 1050 | Enron IPP 345 | 0.964 | 1.039 | 1.043 | 1.044 | 1.041 |
|  |  | 0.97 | 1.041 | 1.046 | 1.047 | 1.044 |
|  |  | 0.975 | 1.045 | 1.049 | 1.050 | 1.048 |
|  |  | 0.98 | 1.049 | 1.053 | 1.054 | 1.052 |
|  |  | 0.985 | 1.054 | 1.058 | 1.059 | 1.057 |
|  |  | 0.99 | 1.059 | 1.064 | 1.065 | 1.062 |
| 1030 | Morgan Creek 345 | 0.964 | 1.035 | 1.039 | 1.039 | 1.035 |
|  |  | 0.97 | 1.038 | 1.043 | 1.043 | 1.039 |
|  |  | 0.975 | 1.042 | 1.046 | 1.047 | 1.043 |
|  |  | 0.98 | 1.047 | 1.051 | 1.052 | 1.048 |
|  |  | 0.985 | 1.053 | 1.057 | 1.058 | 1.054 |
|  |  | 0.99 | 1.060 | 1.064 | 1.065 | 1.061 |
| 1020 | Odessa EHV 345 | 0.964 | 1.022 | 1.025 | 1.021 | 1.011 |
|  |  | 0.97 | 1.027 | 1.030 | 1.026 | 1.016 |
|  |  | 0.975 | 1.033 | 1.036 | 1.033 | 1.023 |
|  |  | 0.98 | 1.041 | 1.043 | 1.041 | 1.031 |
|  |  | 0.985 | 1.049 | 1.052 | 1.049 | 1.040 |
|  |  | 0.99 | 1.059 | 1.062 | 1.060 | 1.050 |
| 6230 | Mulberry 345 | 0.964 | 1.039 | 1.043 | 1.044 | 1.043 |
|  |  | 0.97 | 1.041 | 1.045 | 1.047 | 1.045 |
|  |  | 0.975 | 1.043 | 1.048 | 1.049 | 1.048 |
|  |  | 0.98 | 1.047 | 1.051 | 1.053 | 1.051 |
|  |  | 0.985 | 1.051 | 1.054 | 1.056 | 1.055 |
|  |  | 0.99 | 1.054 | 1.059 | 1.061 | 1.059 |
| 1025 | FS Cogen 345 | 0.964 | 1.032 | 1.035 | 1.035 | 1.030 |
|  |  | 0.97 | 1.035 | 1.038 | 1.038 | 1.033 |
|  |  | 0.975 | 1.039 | 1.041 | 1.041 | 1.037 |
|  |  | 0.98 | 1.043 | 1.045 | 1.046 | 1.042 |
|  |  | 0.985 | 1.048 | 1.050 | 1.050 | 1.047 |
|  |  | 0.99 | 1.054 | 1.056 | 1.056 | 1.052 |
| 1018 | Moss 345 | 0.964 | 1.011 | 1.014 | 1.011 | 1.000 |
|  |  | 0.97 | 1.016 | 1.020 | 1.016 | 1.006 |
|  |  | 0.975 | 1.023 | 1.026 | 1.022 | 1.013 |
|  |  | 0.98 | 1.032 | 1.033 | 1.031 | 1.021 |
|  |  | 0.985 | 1.040 | 1.042 | 1.039 | 1.031 |
|  |  | 0.99 | 1.051 | 1.053 | 1.050 | 1.052 |
| 1021 | Midland 345 | 0.964 | 1.012 | 1.015 | 1.014 | 1.004 |
|  |  | 0.97 | 1.017 | 1.020 | 1.018 | 1.010 |
|  |  | 0.975 | 1.023 | 1.025 | 1.024 | 1.016 |
|  |  | 0.98 | 1.031 | 1.032 | 1.031 | 1.024 |
|  |  | 0.985 | 1.038 | 1.040 | 1.039 | 1.031 |
|  |  | 0.99 | 1.047 | 1.049 | 1.047 | 1.040 |
| 6021 | Indian Mesa 138 | 0.964 | 1.006 | 1.009 | 1.011 | 1.012 |
|  |  | 0.97 | 1.007 | 1.010 | 1.011 | 1.012 |
|  |  | 0.975 | 1.011 | 1.010 | 1.011 | 1.013 |
|  |  | 0.98 | 1.008 | 1.010 | 1.011 | 1.013 |
|  |  | 0.985 | 1.011 | 1.010 | 1.012 | 1.013 |
|  |  | 0.99 | 1.012 | 1.011 | 1.012 | 1.013 |
| 6022 | IndM1 T4 138 | 0.964 | 1.006 | 1.009 | 1.011 | 1.012 |
|  |  | 0.97 | 1.007 | 1.010 | 1.011 | 1.012 |
|  |  | 0.975 | 1.011 | 1.010 | 1.011 | 1.013 |
|  |  | 0.98 | 1.008 | 1.010 | 1.011 | 1.013 |
|  |  | 0.985 | 1.011 | 1.010 | 1.012 | 1.013 |
|  |  | 0.99 | 1.012 | 1.011 | 1.012 | 1.013 |
| 6582 | MesaView2 138 | 0.964 | 1.006 | 1.009 | 1.010 | 1.011 |
|  |  | 0.97 | 1.007 | 1.010 | 1.011 | 1.011 |
|  |  | 0.975 | 1.011 | 1.010 | 1.011 | 1.012 |
|  |  | 0.98 | 1.009 | 1.011 | 1.011 | 1.012 |
|  |  | 0.985 | 1.011 | 1.011 | 1.011 | 1.012 |
|  |  | 0.99 | 1.012 | 1.011 | 1.011 | 1.012 |
| 6583 | Mesa View 138 | 0.964 | 1.006 | 1.009 | 1.010 | 1.011 |
|  |  | 0.97 | 1.007 | 1.010 | 1.011 | 1.011 |
|  |  | 0.975 | 1.011 | 1.010 | 1.011 | 1.011 |
|  |  | 0.98 | 1.008 | 1.010 | 1.011 | 1.012 |
|  |  | 0.985 | 1.011 | 1.010 | 1.011 | 1.012 |
|  |  | 0.99 | 1.012 | 1.011 | 1.011 | 1.012 |
| 6019 | Orion 138 | 0.964 | 1.005 | 1.008 | 1.008 | 1.010 |
|  |  | 0.97 | 1.006 | 1.009 | 1.009 | 1.010 |
|  |  | 0.975 | 1.010 | 1.009 | 1.009 | 1.010 |
|  |  | 0.98 | 1.008 | 1.009 | 1.009 | 1.011 |
|  |  | 0.985 | 1.010 | 1.009 | 1.009 | 1.011 |
|  |  | 0.99 | 1.011 | 1.009 | 1.009 | 1.011 |
| 6578 | Ft Lancaster 69 | 0.964 | 1.006 | 1.014 | 1.017 | 1.017 |
|  |  | 0.97 | 1.007 | 1.015 | 1.018 | 1.018 |
|  |  | 0.975 | 1.011 | 1.015 | 1.018 | 1.018 |
|  |  | 0.98 | 1.009 | 1.015 | 1.017 | 1.019 |
|  |  | 0.985 | 1.011 | 1.015 | 1.018 | 1.019 |
|  |  | 0.99 | 1.012 | 1.016 | 1.018 | 1.019 |
| 6579 | Ft Lancster 138 | 0.964 | 1.006 | 1.009 | 1.009 | 1.007 |
|  |  | 0.97 | 1.007 | 1.010 | 1.009 | 1.008 |
|  |  | 0.975 | 1.011 | 1.010 | 1.010 | 1.008 |
|  |  | 0.98 | 1.008 | 1.010 | 1.010 | 1.008 |
|  |  | 0.985 | 1.011 | 1.010 | 1.010 | 1.008 |
|  |  | 0.99 | 1.011 | 1.010 | 1.010 | 1.008 |
| 60004 | King NE 138 | 0.964 | 1.005 | 1.006 | 1.006 | 1.006 |
|  |  | 0.97 | 1.006 | 1.007 | 1.007 | 1.007 |
|  |  | 0.975 | 1.010 | 1.007 | 1.007 | 1.007 |
|  |  | 0.98 | 1.008 | 1.007 | 1.007 | 1.007 |
|  |  | 0.985 | 1.010 | 1.007 | 1.007 | 1.007 |
|  |  | 0.99 | 1.011 | 1.007 | 1.007 | 1.007 |
| 38380 | Puckittap 69 | 0.964 | 1.014 | 1.013 | 1.006 | 1.000 |
|  |  | 0.97 | 1.016 | 1.015 | 1.008 | 1.002 |
|  |  | 0.975 | 1.020 | 1.014 | 1.009 | 1.003 |
|  |  | 0.98 | 1.017 | 1.015 | 1.009 | 1.003 |
|  |  | 0.985 | 1.020 | 1.015 | 1.009 | 1.003 |
|  |  | 0.99 | 1.021 | 1.016 | 1.009 | 1.004 |
| 38390 | Armadillo 69 | 0.964 | 1.014 | 1.012 | 1.005 | 1.000 |
|  |  | 0.97 | 1.016 | 1.015 | 1.008 | 1.002 |
|  |  | 0.975 | 1.020 | 1.014 | 1.008 | 1.003 |
|  |  | 0.98 | 1.017 | 1.015 | 1.009 | 1.003 |
|  |  | 0.985 | 1.020 | 1.014 | 1.009 | 1.003 |
|  |  | 0.99 | 1.021 | 1.016 | 1.009 | 1.003 |
| 6584 | IndianMesa2 138 | 0.964 | 1.003 | 1.005 | 1.004 | 1.005 |
|  |  | 0.97 | 1.005 | 1.006 | 1.005 | 1.005 |
|  |  | 0.975 | 1.008 | 1.006 | 1.005 | 1.006 |
|  |  | 0.98 | 1.006 | 1.006 | 1.006 | 1.006 |
|  |  | 0.985 | 1.009 | 1.006 | 1.006 | 1.006 |
|  |  | 0.99 | 1.009 | 1.007 | 1.006 | 1.006 |
| 6500 | Live Oak 138 | 0.964 | 1.036 | 1.038 | 1.036 | 1.028 |
|  |  | 0.97 | 1.037 | 1.039 | 1.038 | 1.030 |
|  |  | 0.975 | 1.040 | 1.041 | 1.039 | 1.031 |
|  |  | 0.98 | 1.038 | 1.039 | 1.038 | 1.033 |
|  |  | 0.985 | 1.038 | 1.041 | 1.040 | 1.035 |
|  |  | 0.99 | 1.040 | 1.041 | 1.039 | 1.034 |
| 6577 | Sheffield 69 | 0.964 | 1.001 | 1.008 | 1.011 | 1.011 |
|  |  | 0.97 | 1.003 | 1.009 | 1.012 | 1.012 |
|  |  | 0.975 | 1.006 | 1.009 | 1.012 | 1.012 |
|  |  | 0.98 | 1.004 | 1.009 | 1.012 | 1.012 |
|  |  | 0.985 | 1.006 | 1.010 | 1.012 | 1.013 |
|  |  | 0.99 | 1.007 | 1.010 | 1.012 | 1.013 |
| 6630 | Ft Stockton 138 | 0.964 | 1.014 | 1.012 | 1.005 | 0.999 |
|  |  | 0.97 | 1.015 | 1.014 | 1.007 | 1.001 |
|  |  | 0.975 | 1.019 | 1.014 | 1.007 | 1.001 |
|  |  | 0.98 | 1.017 | 1.014 | 1.008 | 1.002 |
|  |  | 0.985 | 1.020 | 1.014 | 1.008 | 1.002 |
|  |  | 0.99 | 1.020 | 1.015 | 1.008 | 1.002 |
| 38320 | 16th St 69 | 0.964 | 1.013 | 1.011 | 1.004 | 0.999 |
|  |  | 0.97 | 1.014 | 1.013 | 1.006 | 1.001 |
|  |  | 0.975 | 1.018 | 1.013 | 1.007 | 1.001 |
|  |  | 0.98 | 1.016 | 1.013 | 1.007 | 1.002 |
|  |  | 0.985 | 1.019 | 1.013 | 1.007 | 1.001 |
|  |  | 0.99 | 1.019 | 1.014 | 1.007 | 1.002 |
| 38340 | Airport 138 | 0.964 | 1.013 | 1.011 | 1.004 | 0.999 |
|  |  | 0.97 | 1.015 | 1.014 | 1.006 | 1.001 |
|  |  | 0.975 | 1.019 | 1.013 | 1.007 | 1.001 |
|  |  | 0.98 | 1.016 | 1.014 | 1.007 | 1.002 |
|  |  | 0.985 | 1.019 | 1.013 | 1.008 | 1.001 |
|  |  | 0.99 | 1.020 | 1.015 | 1.008 | 1.002 |

Appendix L Fall Off-Peak Voltages for Varying Windpower and Oncor Load Power-Factors for Existing Windpower Modeled with 95% Reactive Power Capability

| Bus per unit Voltages, Fall Off-Peak, Varying Wind |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| and Oncor load power factor |  |  |  | Wind pf = .95 |  |  |
| Number | Bus name, nominal kV | Oncor load pf | wind = 20% nameplate | wind = 40% nameplate | wind = 60% nameplate | wind = 80% nameplate |
| 6009 | Twin Buttes 345 | 0.964 | 1.043 | 1.048 | 1.049 | 1.047 |
|  |  | 0.97 | 1.045 | 1.051 | 1.052 | 1.049 |
|  |  | 0.975 | 1.048 | 1.053 | 1.055 | 1.052 |
|  |  | 0.98 | 1.052 | 1.057 | 1.059 | 1.056 |
|  |  | 0.985 | 1.055 | 1.061 | 1.063 | 1.060 |
|  |  | 0.99 | 1.061 | 1.067 | 1.068 | 1.065 |
| 1420 | Sweetwater 345 | 0.964 | 1.040 | 1.045 | 1.045 | 1.042 |
|  |  | 0.97 | 1.043 | 1.048 | 1.049 | 1.045 |
|  |  | 0.975 | 1.046 | 1.051 | 1.052 | 1.050 |
|  |  | 0.98 | 1.051 | 1.055 | 1.057 | 1.054 |
|  |  | 0.985 | 1.055 | 1.061 | 1.062 | 1.060 |
|  |  | 0.99 | 1.062 | 1.067 | 1.069 | 1.065 |
| 6444 | Red Creek 345 | 0.964 | 1.041 | 1.047 | 1.048 | 1.046 |
|  |  | 0.97 | 1.043 | 1.049 | 1.050 | 1.048 |
|  |  | 0.975 | 1.045 | 1.051 | 1.053 | 1.051 |
|  |  | 0.98 | 1.050 | 1.055 | 1.057 | 1.054 |
|  |  | 0.985 | 1.053 | 1.059 | 1.060 | 1.058 |
|  |  | 0.99 | 1.057 | 1.064 | 1.065 | 1.062 |
| 1050 | Enron IPP 345 | 0.964 | 1.038 | 1.043 | 1.044 | 1.041 |
|  |  | 0.97 | 1.041 | 1.046 | 1.047 | 1.044 |
|  |  | 0.975 | 1.044 | 1.049 | 1.050 | 1.048 |
|  |  | 0.98 | 1.049 | 1.053 | 1.054 | 1.052 |
|  |  | 0.985 | 1.053 | 1.058 | 1.059 | 1.057 |
|  |  | 0.99 | 1.058 | 1.064 | 1.065 | 1.062 |
| 1030 | Morgan Creek 345 | 0.964 | 1.035 | 1.039 | 1.039 | 1.035 |
|  |  | 0.97 | 1.038 | 1.043 | 1.043 | 1.039 |
|  |  | 0.975 | 1.042 | 1.046 | 1.047 | 1.043 |
|  |  | 0.98 | 1.047 | 1.051 | 1.052 | 1.048 |
|  |  | 0.985 | 1.052 | 1.057 | 1.058 | 1.054 |
|  |  | 0.99 | 1.059 | 1.064 | 1.065 | 1.061 |
| 1020 | Odessa EHV 345 | 0.964 | 1.021 | 1.025 | 1.021 | 1.011 |
|  |  | 0.97 | 1.026 | 1.030 | 1.026 | 1.016 |
|  |  | 0.975 | 1.032 | 1.036 | 1.033 | 1.023 |
|  |  | 0.98 | 1.040 | 1.043 | 1.041 | 1.031 |
|  |  | 0.985 | 1.047 | 1.052 | 1.049 | 1.040 |
|  |  | 0.99 | 1.057 | 1.062 | 1.060 | 1.050 |
| 6230 | Mulberry 345 | 0.964 | 1.038 | 1.043 | 1.044 | 1.043 |
|  |  | 0.97 | 1.041 | 1.045 | 1.047 | 1.045 |
|  |  | 0.975 | 1.043 | 1.048 | 1.049 | 1.048 |
|  |  | 0.98 | 1.046 | 1.051 | 1.053 | 1.051 |
|  |  | 0.985 | 1.049 | 1.054 | 1.056 | 1.055 |
|  |  | 0.99 | 1.054 | 1.059 | 1.061 | 1.059 |
| 1025 | FS Cogen 345 | 0.964 | 1.032 | 1.035 | 1.035 | 1.030 |
|  |  | 0.97 | 1.034 | 1.038 | 1.038 | 1.033 |
|  |  | 0.975 | 1.038 | 1.041 | 1.041 | 1.037 |
|  |  | 0.98 | 1.042 | 1.045 | 1.046 | 1.042 |
|  |  | 0.985 | 1.047 | 1.050 | 1.050 | 1.047 |
|  |  | 0.99 | 1.052 | 1.056 | 1.056 | 1.052 |
| 1018 | Moss 345 | 0.964 | 1.011 | 1.014 | 1.011 | 1.000 |
|  |  | 0.97 | 1.016 | 1.019 | 1.016 | 1.006 |
|  |  | 0.975 | 1.022 | 1.026 | 1.022 | 1.013 |
|  |  | 0.98 | 1.030 | 1.033 | 1.031 | 1.021 |
|  |  | 0.985 | 1.037 | 1.042 | 1.039 | 1.031 |
|  |  | 0.99 | 1.048 | 1.053 | 1.050 | 1.040 |
| 1021 | Midland 345 | 0.964 | 1.011 | 1.015 | 1.014 | 1.004 |
|  |  | 0.97 | 1.015 | 1.020 | 1.018 | 1.010 |
|  |  | 0.975 | 1.022 | 1.025 | 1.024 | 1.016 |
|  |  | 0.98 | 1.029 | 1.032 | 1.031 | 1.024 |
|  |  | 0.985 | 1.035 | 1.040 | 1.039 | 1.031 |
|  |  | 0.99 | 1.045 | 1.049 | 1.047 | 1.040 |
| 6021 | Indian Mesa 138 | 0.964 | 1.005 | 1.009 | 1.011 | 1.012 |
|  |  | 0.97 | 1.006 | 1.010 | 1.011 | 1.012 |
|  |  | 0.975 | 1.006 | 1.010 | 1.011 | 1.013 |
|  |  | 0.98 | 1.006 | 1.010 | 1.011 | 1.013 |
|  |  | 0.985 | 1.006 | 1.010 | 1.012 | 1.013 |
|  |  | 0.99 | 1.006 | 1.010 | 1.012 | 1.013 |
| 6022 | IndM1 T4 138 | 0.964 | 1.005 | 1.009 | 1.011 | 1.012 |
|  |  | 0.97 | 1.006 | 1.010 | 1.011 | 1.012 |
|  |  | 0.975 | 1.006 | 1.010 | 1.011 | 1.013 |
|  |  | 0.98 | 1.006 | 1.010 | 1.011 | 1.013 |
|  |  | 0.985 | 1.006 | 1.010 | 1.012 | 1.013 |
|  |  | 0.99 | 1.006 | 1.010 | 1.012 | 1.013 |
| 6582 | MesaView2 138 | 0.964 | 1.005 | 1.009 | 1.010 | 1.011 |
|  |  | 0.97 | 1.006 | 1.010 | 1.011 | 1.011 |
|  |  | 0.975 | 1.006 | 1.010 | 1.011 | 1.012 |
|  |  | 0.98 | 1.006 | 1.010 | 1.011 | 1.012 |
|  |  | 0.985 | 1.007 | 1.010 | 1.011 | 1.012 |
|  |  | 0.99 | 1.007 | 1.010 | 1.011 | 1.012 |
| 6583 | Mesa View 138 | 0.964 | 1.005 | 1.009 | 1.010 | 1.011 |
|  |  | 0.97 | 1.006 | 1.010 | 1.011 | 1.011 |
|  |  | 0.975 | 1.006 | 1.010 | 1.011 | 1.011 |
|  |  | 0.98 | 1.006 | 1.010 | 1.011 | 1.012 |
|  |  | 0.985 | 1.007 | 1.010 | 1.011 | 1.012 |
|  |  | 0.99 | 1.006 | 1.010 | 1.011 | 1.012 |
| 6019 | Orion 138 | 0.964 | 1.004 | 1.007 | 1.008 | 1.010 |
|  |  | 0.97 | 1.005 | 1.008 | 1.009 | 1.010 |
|  |  | 0.975 | 1.005 | 1.008 | 1.009 | 1.010 |
|  |  | 0.98 | 1.005 | 1.008 | 1.009 | 1.011 |
|  |  | 0.985 | 1.005 | 1.008 | 1.009 | 1.011 |
|  |  | 0.99 | 1.005 | 1.009 | 1.009 | 1.011 |
| 6578 | Ft Lancaster 69 | 0.964 | 1.005 | 1.014 | 1.017 | 1.017 |
|  |  | 0.97 | 1.006 | 1.014 | 1.018 | 1.018 |
|  |  | 0.975 | 1.007 | 1.015 | 1.018 | 1.018 |
|  |  | 0.98 | 1.006 | 1.015 | 1.018 | 1.019 |
|  |  | 0.985 | 1.007 | 1.015 | 1.018 | 1.019 |
|  |  | 0.99 | 1.007 | 1.015 | 1.018 | 1.019 |
| 6579 | Ft Lancster 138 | 0.964 | 1.005 | 1.008 | 1.009 | 1.007 |
|  |  | 0.97 | 1.006 | 1.009 | 1.009 | 1.008 |
|  |  | 0.975 | 1.006 | 1.009 | 1.010 | 1.008 |
|  |  | 0.98 | 1.006 | 1.009 | 1.010 | 1.008 |
|  |  | 0.985 | 1.006 | 1.010 | 1.010 | 1.008 |
|  |  | 0.99 | 1.006 | 1.010 | 1.010 | 1.008 |
| 60004 | King NE 138 | 0.964 | 1.004 | 1.006 | 1.006 | 1.006 |
|  |  | 0.97 | 1.004 | 1.006 | 1.007 | 1.007 |
|  |  | 0.975 | 1.005 | 1.006 | 1.007 | 1.007 |
|  |  | 0.98 | 1.005 | 1.007 | 1.007 | 1.007 |
|  |  | 0.985 | 1.005 | 1.007 | 1.007 | 1.007 |
|  |  | 0.99 | 1.005 | 1.007 | 1.007 | 1.007 |
| 38380 | Puckittap 69 | 0.964 | 1.013 | 1.011 | 1.006 | 1.000 |
|  |  | 0.97 | 1.015 | 1.013 | 1.008 | 1.002 |
|  |  | 0.975 | 1.016 | 1.014 | 1.009 | 1.003 |
|  |  | 0.98 | 1.016 | 1.014 | 1.009 | 1.003 |
|  |  | 0.985 | 1.017 | 1.014 | 1.009 | 1.003 |
|  |  | 0.99 | 1.017 | 1.015 | 1.009 | 1.004 |
| 38390 | Armadillo 69 | 0.964 | 1.013 | 1.011 | 1.005 | 1.000 |
|  |  | 0.97 | 1.015 | 1.013 | 1.008 | 1.002 |
|  |  | 0.975 | 1.016 | 1.014 | 1.008 | 1.003 |
|  |  | 0.98 | 1.016 | 1.014 | 1.009 | 1.003 |
|  |  | 0.985 | 1.017 | 1.014 | 1.009 | 1.003 |
|  |  | 0.99 | 1.017 | 1.015 | 1.009 | 1.003 |
| 6584 | IndianMesa2 138 | 0.964 | 1.003 | 1.005 | 1.004 | 1.005 |
|  |  | 0.97 | 1.003 | 1.005 | 1.005 | 1.005 |
|  |  | 0.975 | 1.004 | 1.006 | 1.005 | 1.006 |
|  |  | 0.98 | 1.004 | 1.006 | 1.006 | 1.006 |
|  |  | 0.985 | 1.004 | 1.006 | 1.006 | 1.006 |
|  |  | 0.99 | 1.004 | 1.006 | 1.006 | 1.006 |
| 6500 | Live Oak 138 | 0.964 | 1.035 | 1.037 | 1.036 | 1.028 |
|  |  | 0.97 | 1.037 | 1.039 | 1.038 | 1.030 |
|  |  | 0.975 | 1.039 | 1.041 | 1.039 | 1.031 |
|  |  | 0.98 | 1.037 | 1.039 | 1.038 | 1.033 |
|  |  | 0.985 | 1.039 | 1.041 | 1.040 | 1.035 |
|  |  | 0.99 | 1.039 | 1.041 | 1.039 | 1.034 |
| 6577 | Sheffield 69 | 0.964 | 1.000 | 1.008 | 1.011 | 1.011 |
|  |  | 0.97 | 1.001 | 1.009 | 1.012 | 1.012 |
|  |  | 0.975 | 1.002 | 1.009 | 1.012 | 1.012 |
|  |  | 0.98 | 1.002 | 1.009 | 1.012 | 1.012 |
|  |  | 0.985 | 1.002 | 1.009 | 1.012 | 1.013 |
|  |  | 0.99 | 1.002 | 1.009 | 1.012 | 1.013 |
| 6630 | Ft Stockton 138 | 0.964 | 1.013 | 1.010 | 1.005 | 0.999 |
|  |  | 0.97 | 1.015 | 1.013 | 1.007 | 1.001 |
|  |  | 0.975 | 1.016 | 1.013 | 1.007 | 1.001 |
|  |  | 0.98 | 1.016 | 1.014 | 1.008 | 1.002 |
|  |  | 0.985 | 1.017 | 1.013 | 1.008 | 1.002 |
|  |  | 0.99 | 1.017 | 1.014 | 1.008 | 1.002 |
| 38320 | 16th St 69 | 0.964 | 1.012 | 1.010 | 1.004 | 0.999 |
|  |  | 0.97 | 1.014 | 1.012 | 1.006 | 1.001 |
|  |  | 0.975 | 1.015 | 1.012 | 1.007 | 1.001 |
|  |  | 0.98 | 1.015 | 1.013 | 1.007 | 1.002 |
|  |  | 0.985 | 1.016 | 1.012 | 1.007 | 1.001 |
|  |  | 0.99 | 1.016 | 1.013 | 1.007 | 1.002 |
| 38340 | Airport 138 | 0.964 | 1.012 | 1.010 | 1.004 | 0.999 |
|  |  | 0.97 | 1.014 | 1.012 | 1.006 | 1.001 |
|  |  | 0.975 | 1.015 | 1.013 | 1.007 | 1.001 |
|  |  | 0.98 | 1.015 | 1.013 | 1.007 | 1.002 |
|  |  | 0.985 | 1.016 | 1.013 | 1.008 | 1.001 |
|  |  | 0.99 | 1.016 | 1.014 | 1.008 | 1.002 |