ERCOT Operations Report

ROS & OWG

For March 2003

Frequency control issues (High or Low Frequency) 59.9 > F > 60.1

| Time | Frequency | Event | Load | Reg | SCE |
| --- | --- | --- | --- | --- | --- |
| 3/1/2003 1:54 | 59.69599915 | Unit trip carrying 1250+ MW | N/A | N/A | N/A |
| 3/3/2003 22:04 | 59.84799957 |  | Decreasing | -130(Increasing) | -1108 |
| 3/3/2003 22:58 | 60.10599899 |  | Decreasing | -1330(Constant) | 595 |
| 3/4/2003 6:09 | 59.88399887 |  | Increasing | -760(Increasing) | -1004 |
| 3/5/2003 6:08 | 59.86700058 |  | Increasing | 154(Increasing) | -794 |
| 3/5/2003 22:06 | 59.83399963 |  | Decreasing | 90(Increasing) | -1855 |
| 3/7/2003 22:08 | 59.875 |  | Decreasing | 395 (Increasing) | 932 |
| 3/9/2003 15:05 | 59.86600113 | 570 MW Unit tripped | N/A | N/A | N/A |
| 3/10/2003 22:08 | 59.88700104 |  | Decreasing | -300(Increasing) | -529 |
| 3/13/2003 6:01 | 60.11100006 | N/A |  |  | 1633 |
| 3/13/2003 22:01 | 59.88499832 |  | Decreasing | -350(Increasing) | -615 |
| 3/14/2003 5:57 | 60.10900116 | N/A |  |  | 684 |
| 3/14/2003 22:06 | 59.81399918 |  | Constant | 790(Increasing) | -1221 |
| 3/14/2003 22:20 | 60.14500046 |  | Constant | 380(Decreasing) | 826 |
| 3/15/2003 19:29 | 60.10200119 | N/A |  |  | 244 |
| 3/15/2003 19:49 | 59.86500168 | 750 MW unit runback and trip. | N/A | N/A | N/A |
| 3/15/2003 19:53 | 60.13100052 | Overshoot from unit trip | N/A | N/A | N/A |
| 3/16/2003 21:49 | 59.72100067 | 1150 MW unit trip |  |  | N/A |
| 3/16/2003 21:56 | 60.13899994 | Overshoot from unit trip |  |  | N/A |
| 3/17/2003 12:11 | 60.10300064 |  |  |  | 309 |
| 3/18/2003 4:15 | 59.88499832 |  |  |  | 12 |
| 3/18/2003 9:12 | 59.82699966 | 450 MW unit tripped | N/A | N/A | N/A |
| 3/18/2003 22:02 | 59.82899857 |  | Decreasing | 380(Increasing) | -728 |
| 3/24/2003 22:59 | 60.10100174 |  | Decreasing | -95(Decreasing) | 426 |
| 3/25/2003 6:08 | 59.89799881 |  |  |  | -93 |
| 3/25/2003 22:03 | 59.8730011 |  | Oscillating | -85(Increasing) | -702 |
| 3/28/2003 22:10 | 60.10699844 |  | Decreasing | 370(Decreasing) | 320 |
| 3/29/2003 2:49 | 59.85499954 | 415 MW unit tripped. | N/A | N/A | N/A |

Following the unit trips of 3/15, 3/16 and 2/21 ERCOT system frequency overshot 60 Hz by more than .1 Hz. On 3/18 ERCOT adjusted the responsive gain from 1 to .66 to correct this overshoot by reducing the amount of responsive deployed.

# Locations and Relative Activity of Congestion Management

*Days of units purchased for some time in the area described.  Data taken from daily reports and is approximate.  For global overview purposes only.

New Procedures/ Forms/ Operations Bulletins

3/06	Operations Bulletin 15 posted.  Revisions made to Transmission Security section of the Operating Procedure Manual adding the Forced/Level 1 Outage Information Sheet (Appendix 8).

3/26	Operations Bulletin 16 posted.  Change involves QSE’s giving ERCOT one hour prior to taking a resource off line in order to allow ERCOT time to evaluate the impact on system reliability.

Security Alert Stage/ Threatcon/ Related issues

3/17 20:00    Homeland Security and NERC raised their levels from Yellow (Elevated) to Orange (High). 3/18 10:00    ERCOT raised to Medium Modified Alert.

3/21 14:00    Security Threat Alert Level Orange Issued.

Describe each EECP Occurrence

None.

OCN, Advisory, Alert, Energy Notice and Major Disturbances

3/6    06:48 – 08:30 Generation Insufficiency Alert issued.

3/6 06:48 – 09:00 OC Congestion Alert issued.  Exceeded South to North limit due to the insufficiency of

generation.

3/6    07:03   Market Alert due to insufficiency of up balancing.

3/6     07:17   Transmission Alert due to exceeding operational limits.

3/11   09:25   Communication Alert due to portal being down.

3/18 10:00   Alert issued ERCOT raised Security level to Medium Modified.

Major Weather Related Power System Problems

None.

Significant Communication Problems

3/11 	Communication Alert due to portal being down

Major Computer Systems Problems/ Fixes

3/1 	MOI down, held 00:45 Interval for 01:00.

3/1	MOI down, held 20:15 Interval for 20:30.

3/3	MOI down, Portal down.  Held 13:15 Interval through 14:00.

3/4	Held interval 1930, resumed with 2030 for Build 3 migration.

3/7	Held Balancing deployments 02:30 – 03:00 due to MOI problem

3/18	Held Balancing deployments 02:30 – 04:00 due to MOI problem.

3/30	Balancing Energy Market held due to computer problem.

Major system Voltage problems

None

Blackout/Load Shed incidences

None

ERCOT peak for last month (Unofficial)

3/6   8:00	36605 (from Daily Operations Report)

Update on New Generation

No new generation approved for initial synchronization in March.

Max / Min Temperature

3/18   88 F (Brownsville)

3/5     25 F (Abilene)

# New SPS & RAP’s

None.

## Other

3/18	Adjusted system gain at 09:35.

3/19	Smoothing Algorithm implemented at 10:15.

3/25       Balancing Deployments held 22:15 – 22:30 due to bad telemetry.

## Limits Exceeded

| Interzonal Transfer | Start Time | End Time | Time Over Limit |
| --- | --- | --- | --- |
| Valley Import | 3/1/2003 23:52 | 3/2/2003 0:26 | 34 |
| Valley Import | 3/3/2003 23:23 | 3/4/2003 0:09 | 46 |
| Valley Import | 3/4/2003 2:47 | 3/4/2003 3:31 | 44 |
| Valley Import | 3/4/2003 3:46 | 3/4/2003 4:26 | 40 |
| South-North | 3/6/2003 4:02 | 3/6/2003 4:39 | 37 |
| South-North | 3/6/2003 6:10 | 3/6/2003 8:50 | 160 |
| West - East (Morgan - East) | 3/6/2003 6:51 | 3/6/2003 8:13 | 82 |
| South-North | 3/6/2003 19:01 | 3/6/2003 20:28 | 87 |
| South-North | 3/7/2003 9:27 | 3/7/2003 10:11 | 44 |
| South - Houston | 3/9/2003 11:41 | 3/9/2003 14:44 | 183 |
| South-North | 3/12/2003 16:56 | 3/12/2003 17:27 | 31 |
| South-North | 3/17/2003 7:57 | 3/17/2003 8:28 | 31 |
| South-North | 3/17/2003 12:26 | 3/17/2003 12:59 | 33 |
| South-North | 3/18/2003 19:56 | 3/18/2003 20:36 | 40 |
| Valley Import | 3/26/2003 23:14 | 3/26/2003 23:48 | 34 |