| OGRR Number | 134OGRR | OGRR Title | Calculation of Transmission Equipment Limits |
| --- | --- | --- | --- |
| ###### Status |  | Posted |  |
| Operating Guide Section Requiring Revision |  | 3.1.6 |  |
| Protocol Section Requiring Revision, if any. |  |  |  |
| Requested Resolution |  | ## Revise section 3.1.6 as shown |  |
| Revision Description |  | Defines equipment ratings for TDSP’s facilities and ERCOT’s use of the ratings. |  |
| ###### Reason for Revision |  | The limits, which ERCOT is responsible for maintaining are currently very unclear; and do not address NERC requirements regarding Operating System Limits and Interconnection Reliability Limits. This change allows ERCOT to operate in a transparent mode and maximizes transmission utilization. |  |
| ## Sponsor |  |  |  |
| Name |  | John Adams |  |
| E-mail Address |  | jadams@ercot.com |  |
| Company |  | ERCOT |  |
| Company Address |  | 2705 West Lake Drive |  |
| Phone Number |  | 512 248-3130 |  |
| Fax Number |  | 512 248-3055 |  |
| ## Timeline |  |  |  |
| Date Received |  | 4/14/2003 |  |
| Date Posted |  | 4/18/2003 |  |
| OGRTF Review |  | 5/21/2003 |  |
| OWG Review |  | 5/22/2003 |  |
| ROS Review Date |  | 6/11/2003 |  |
| ROS Recommendation |  |  |  |
| Other Subcommittee Consideration |  | 6/19/2003 [PRS] |  |
| TAC Consideration |  | 7/02/2003 |  |

Proposed Operating Guide Language Revision

### 3.1.6	Responsibility For Equipment Ratings

TDSPs are responsible for determining the rating of their facilities.

Technical limits established for the operation of transmission equipment shall be applied consistently in TTC calculations, engineering studies, real-time security analyses, and operator actions.

TDSP’s shall provide ERCOT with three (3) equipment Ratings:

- Normal Rating:  Represents the continuous MW rating of a piece of equipment at the applicable temperature range, which the equipment can operate indefinitely without damage, or violation of clearances.  This rating will used in all the Steady State Working Group Base Cases as RATE-A

- Emergency Rating:  Represents the rating a piece of equipment can accept at the applicable ambient temperature range; which the equipment can operate for two (2) hours without violation of safety rules (clearances) or equipment failure.  This rating will used in all the Steady State Working Group Base Cases as RATE-B

- Load Shed Rating:  Represents the maximum MW transfer a piece of equipment can withstand for 15 minutes assuming its pre-contingency loading was 90% of the normal limit at the applicable ambient temperature, without violation of safety rules (clearances) or equipment failure. This rating will used in all the Steady State Working Group Base Cases as RATE-C

- ERCOT shall use these ratings as follows:

- ERCOT shall limit pre-contingency flows to enforce the normal rating.

- If no Remedial Action Plan exists to unload a piece of equipment post contingency, ERCOT shall enforce pre-contingency System Operating Limit(s) to control the post contingency loading of a piece of equipment to levels below the Emergency Rating.

- If a Remedial Action Plan is documented at ERCOT to relieve the loading on the piece of equipment within 15 minutes; ERCOT shall enforce pre-contingency System Operating Limit(s) to control the post contingency loading of a piece of equipment to levels below the Load Shed Limit.

By January 2005, TO’s; in cooperation with ERCOT, shall implement dynamic transmission equipment rating to include the effect of ambient temperature upon transmission equipment ratings.

| ## Other TAC Subcommittee Review |  |
| --- | --- |
| PRS Review Date |  |
| PRS Protocols Impact Decision |  |
| WMS Review Date |  |
| RMS Review Date |  |
| ## TAC Action |  |
| TAC Vote Date |  |
| TAC Proposed Implementation Date |  |
| TAC Vote Results |  |
| ## ERCOT Board Action |  |
| ERCOT Board Vote Date |  |
| ERCOT Board Implementation Date |  |
| ERCOT Board Results |  |
| ## Appeal |  |
| Appeal Date |  |
| Entity Initiating Appeal |  |
| Nature of Appeal |  |