| OGRR Number | 134OGRR | OGRR Title | Calculation of Transmission Equipment Limits |
| --- | --- | --- | --- |
| ###### Date |  |  |  |
| ## Submitter’s Information |  |  |  |
| Name |  | Dennis Kunkel |  |
| E-mail Address |  | dkkunkel@aep.com |  |
| Company |  | AEP |  |
| Company Address |  | 5502 Corporate Dr |  |
| Phone Number |  | 361 289 4003 |  |
| Fax Number |  | 361 289 4030 |  |

Comments

AEP agrees with Center Point Comments.

As far as the implementation of the dynamic rating, alarming systems will need to be able to adjust for temperature but also reflect that at some temperatures another component that is not temperature dependant becomes the limitation.  We can handle a dynamic rating for a  limited number of lines now but to say that it should be expanded to all circuits is not taking into account the complexity of the situation and the amount of research needed to find all the non conductor limits (relays, switches, CTS, PTS, etc.).