COMPLIANCE REPORT TO ROS

June 4, 2003

- ERCOT Frequency Control Related Issues:

  - Regulating QSE’s who did not pass 10 minute average are being contacted about need to review performance.  Ditto QSE’s not passing balancing standard.  AS reports for May are being produced, may not be ready for ROS meeting.  These include effect of Protocol exclusions from AS reporting.

  - Target posting date for the new NERC “Balancing” standards is uncertain, delayed from May 15. The comment period will be relatively short (30 days).   Need PDCWG input and comments.

  - ERCOT CPS-1 one-minute average frequency score continues to decline in May.   Fleet deployments and units in test under VDI probably contribute to the further decline.

  - Compliance working with QSE Project Managers on review of regulation, uninstructed resource charges, SCE, and MCPE relationships.

  - Need to work with PDCWG to review ERCOT’s Lsub10, which is used in the 10 minute QSE AS performance measure.

- Transmission Security Issues:

  - Possible NERC reportable violations in May will be presented at the ROS meeting, if there are any.

  - ROS requested a means to track security violations that are significant to the system but not reportable to NERC under the new NERC Interconnect Reliability Limit criteria.  Compliance needs to review methods with Operations, but it should be possible to accumulate time when operating above commonly modeled pre-contingency limits initially.  John Adams developed a list of elements in March that can be used as a starting point.  Historical recording system has still not gone into production mode at ERCOT, which will delay implementation somewhat.

- NERC Compliance program for 2003

  - Self certification for TO’s will be mailed later this summer, due in the Fall.  Compliance will conduct more site reviews on issues than previous years. QSE visits also starting, to review emergency plans, real time data and other issues.

  - Listing of status of NERC standards development will be presented at ROS.

- 2003 Underfrequency load shed survey of TDSP’s was due June 4.  Results to be discussed at ROS.  Issue: is a formal retest necessary?

- Unit Test Scheduling and Testing as required by the Protocols is improving, but there continue to be problems in getting this done consistently.   Compliance stepping up requests for reactive tests.

- Event Investigations -  Compliance is assisting Operations in collecting responses to relay maintenance and review surveys due June 2 to Steve Myers.  Need to validate UFLS operation for all TDSP’s from the May 15th event.   Following up with generators who tripped on May 15th; one reports having an underfrequency relay at the generator operating at 59.4 cycles.

- Resource Plan Performance Metrics – Compliance working with QSEPM’s and ERCOT Mkt Operations on a pilot measure of resource plan accuracy.

- Draft letter for QSE/Gens attached for ROS comments.  Target issue June 12.