| OGRR Number | 134OGRR | OGRR Title | Calculation of Transmission Equipment Limits |
| --- | --- | --- | --- |
| Date |  | May 21, 2003 |  |
| Operating Guide Section Requiring Revision |  | 3.1.6 |  |
| Protocol Section Requiring Revision, if any. |  |  |  |
| Recommended Recommendation |  | ## Approve Section 3.1.6 as revised |  |
| Revision Description |  | Defines equipment ratings for TDSP’s facilities and ERCOT’s use of the ratings. |  |
| ###### Reason for Revision |  | The limits, which ERCOT is responsible for maintaining are currently very unclear; and do not address NERC requirements regarding Operating System Limits and Interconnection Reliability Limits. This change allows ERCOT to operate in a transparent mode and maximizes transmission utilization. |  |

Proposed Operating Guide Language Revision

### 3.1.6	Responsibility For Transmission Facility Ratings

TDSPs are responsible for determining the rating of their facilities.

Technical limits established for the operation of Transmission Facilities shall be applied consistently in TTC calculations, engineering studies, real-time security analyses, and operator actions.

TDSP’s shall provide ERCOT with three (3) nominal Transmission Facility Ratings:

- Continuous Rating:  Represents the continuous MVA rating of a Transmission Facility (including substation terminal equipment in series with a conductor or transformer) at the applicable ambient temperature.   The  Transmission Facility can operate at this rating indefinitely without damage, or violation of National Electrical Safety Code (NESC) clearances.

- Emergency Rating:  Represents the two (2) hour MVA rating of a  Transmission Facility (including substation terminal equipment in series with a conductor or transformer)  at the applicable ambient temperature.  The Transmission Facility can operate at this rating for two (2) hours without violation of NESC clearances or equipment failure.

- Fifteen Minute Rating:  Represents the fifteen (15) minute MVA rating of a Transmission Facility (including substation terminal equipment in series with a conductor or transformer) at the applicable ambient temperature and with a step increase from a prior loading of 90% of the Continuous Rating.  The Transmission Facility can operate at this rating for fifteen (15) minutes, assuming its pre-contingency loading was 90% of the Continuous Rating limit at the applicable ambient temperature, without violation of NESC clearances or equipment failure.  This rating takes advantage of the time delay associated with heating of a conductor or transformer following a sudden increase in current.

- In operating the Transmission Grid, ERCOT shall use these ratings as follows:

- ERCOT shall limit pre-contingency flows to enforce the Continuous Rating.

- If  a valid Remedial Action Plan  is unavailable to unload  the Transmission Facility post contingency or the pre-contingency loading is greater than 90% of the Continuous Rating, ERCOT shall enforce pre-contingency System Operating Limit(s) to control the post contingency loading of the facility to levels below the Emergency Rating. The enforcement shall be implemented in a manner such that the post contingency loading will be at, or below, Continuous Rating within two (2) hours.

- If a Remedial Action Plan is documented at ERCOT to relieve the loading on the  Transmission Facility within fifteen (15) minutes; ERCOT shall enforce pre-contingency System Operating Limit(s) to control the post contingency loading of the facility to levels below the Fifteen Minute Rating.  The enforcement shall be implemented in a manner such that the post contingency loading will be at, or below, Emergency Rating within fifteen (15) minutes.

- ERCOT shall use best efforts to restore all Transmission Facilities to within Continuous Ratings as soon as practicable, based on Good Utility Practice.