COMPLIANCE REPORT TO ROS

July 3, 2003

- ERCOT Frequency Control Related Issues:

  - Regulating QSE’s who did not pass 1 and/or 10 minute average are being contacted about need to review performance based on May performance.  June performance will be sent by the 15th.    Ditto QSE’s apparently not passing balancing standard.  AS reports for June are being produced, may not be ready for ROS meeting.  These include effect of Protocol exclusions from AS reporting and a new Lsub10, which is a constant that affects the 10 minute measure of regulation performance as well as the ERCOT control area’s CPS2 score.

  - The new NERC “Balancing” standard for frequency control  is posted for initial comments due August 29. The comment period was extended to 60 days.   Need PDCWG input and comments.

  - ERCOT CPS-1 monthly one-minute average frequency score continues for June is about the same as May’s, a slight improvement from 110 to 115% (100 is minimum passing, averaged over 12 months.)

  - Compliance continues to work with QSE Project Managers on review of regulation, uninstructed resource charges, SCE, and MCPE relationships.   So far just data gathering.

  - PDCWG has suggested a revision to ERCOT’s Lsub10, which is used in the 10 minute QSE AS performance measure and ERCOT control area measure CPS2.  It is a constant that includes a factor for the acceptable statistical distribution of frequency deviations, based on historical performance.  It has been implemented in the ERCOT control computer.  ERCOT is exempt from CPS2 but the adjustment was made to correlate with earlier changes to the other CPS1 one-minute measure.

  - Compliance is reviewing morning ramp performance with a group of QSE’s who have not followed  ramps well at 0600 and 2000.  There is no performance measure specifically for these; QSE’s not providing Ancillary Services are supposed to make a good faith effort to follow schedules.  Request that PDCWG consider draft development of a performance index or measure based on SCE performance.

- Transmission Security Issues:

  - Operations reports no NERC Interconnect Reliability Limit violations in May.

  - NERC has posted standards for Facility Ratings and Transmission Security Limits,  with comments due August 29. The comment period was extended to 60 days.

- NERC Compliance program for 2003

  - Self certification for TO’s will be mailed later this summer, due in the Fall.  Compliance will conduct more site reviews on issues than previous years. QSE visits also starting, to review emergency plans, real time data and other issues.

  - Listing of status of NERC standards development will be presented at ROS.

- Event Investigations -  Compliance is assisting Operations in collecting responses to relay maintenance and review surveys due June 2 to Steve Myers.  Need to validate UFLS operation for all TDSP’s from the May 15th event, data collection in progress.  Many UF relays did not operate based on what we are getting initially; asking SPWG chair to get additional fault recorder or other device frequency records to validate ERCOT’s recording.

- Resource Plan Performance Metrics – Compliance working with QSEPM’s and ERCOT Mkt Operations on a pilot measure of resource plan accuracy.   TAC/PUCT has made this a priority item and expects a draft compliance measure and enforcement plan by August 1.

- Draft letter for QSE/Gens was sent, delayed until June 30 for incorporation of additional comments from market participants after ROS.  Compliance will be following up on this.