# Report on Status of North-Houston Congestion 7/01/03

# REVIEW OF PROBLEM

At high levels of import into the Houston Zone from the North, a forced outage of the double circuit Roans Prairie to Kuykendahl and Jewett-THW results in severe overloading of the Gibbons Creek to O’Brien 345 kV transmission circuit.  Pre-contingency loading conditions, which would result in post contingency overloads above 130% of emergency rating, have been observed on multiple occasions.

# Operational Changes at ERCOT

In response to recommendations of TAC members at the meeting of 6/4/2003, ERCOT begun issuing Verbal Dispatch Instructions as instructed deviations on 6/6/2003.

Although there was one day of confusion on the meaning of “instructed deviation”, this procedure seems to be working.

ERCOT has proposed creation of a CSC between the North and South zones to the PRS and Technical Advisory Committee for 2003.   TAC did not take action on this recommendation at its meeting of 6/4/2003, but recommended that ERCOT investigate methods of increasing the available flow limit on the North-Houston path.

# Updated History of North-Houston Congestion Occurrences

- 5/8/2003 – 500 MW H

- 5/12/2003 – 1500 MW H

- 5/13/2003 – 1500 MW H

- 5/14/2003 – 300 MW H

- 5/18/2003 – 250 MW N/H

- 5/19/2003  - 200 MW N/H

- 5/20/2003 – 2500 MW N/H

- 5/21/2003 – 2500 MW N/H

- 5/22/03 – OOME individual units solved problem

- 5/23/03 – OOME individual units solved problem

- 5/24/03 – OOME individual units solved problem

- 5/25/03 – 300 MW N/H

- 5/26/03 – 600 MW N/H

- 5/28/03 – 300 MW N/H

- 5/29/03 – OOME individual units solved problem

- 6/01/03 - 300 MW N/H

- 6/02/03 – 300 Mw N/H

- 6/03/03 – 300 MW N/H

- 6/05/03 – 300 MW N/H

- 6/06/03 – 1200 MW N/H Began issuing “instructed deviations”

- 6/07/03 – 306 MW N/H

- 6/08/03 – 318 MW N/H

- 6/09/03 – 465 MW H

- 6/12/03 – 640 MW H / -1500 N

- 6/13/03 – 1115 MW H / -1140 N

- 6/14/03 – 640 MW H /  -449 N

- 6/17/03 – 1509 MW H / -790 N

- 6/18/03 – 533 MW H / -533 N

- 6/23/03 – 350 MW H

- 6/27/03 – 96 MW H (reduced limit to 2000)

Shown graphically this information is as follows.  It appears that the problem becoming less prevalent, particularly when you recognize that one of the remediation actions in the last two weeks was due to a reduced limit.

# Why the North-Houston Import limit is violated less

In the last 30 days, two major modern generating plants have become available in the Houston area.  The first became available in the first week of June, the second on in late June.   These two plants represent approximately 1000 MW of additional economic generation in the Houston Zone, which was not available in May.

# Why North-Houston violations were not forecast in the Day ahead Load flow

One of the issues previously discussed was the failure of ERCOT daily load flow to detect the projected overloads.   ERCOT examines the day ahead using a load flow of peak conditions each day.  Typically, this study is performed for the hour of ~17:00.  The chart shown demonstrates that the average Houston area import, as predicted by actual load minus generation, is minimum at this time.  Since becoming aware of this possibility, the over limit condition has been demonstrated in day-ahead load flow studies.  It has not been detected in methods depending upon shift factors.

Physical flows vs Limit in June

# Footnotes

These two circuits share towers.

In this table, a MW number indicates the Maximum amount of net portfolio energy OOME.  An H alone indicates the net portfolio energy deployment was made in the Houston zone alone.  An N/H indicates the MW net portfolio energy deployment in Houston was matched by an equal and opposite portfolio energy deployment in the North zone.