COMPLIANCE REPORT TO ROS

August 1, 2003

- ERCOT Frequency Control Related Issues:

  - Compliance is working with QSE’s to review responses to letters of non-Compliance for Regulation and Balancing Performance and identify factors affecting the scores.

  - The new NERC “Balancing” standard for frequency control  is posted for initial comments due August 29. The comment period was extended to 60 days.   Need PDCWG input and comments.

  - ERCOT CPS-1 monthly one-minute average frequency score apparently jumped to nearly 140%, up from 115%  in June.  (100 is minimum passing, averaged over 12 months.)

- Transmission Security Issues:

  - Review of June CSC flows for NERC Interconnect Reliability Limit violations is in progress.  Since revising the criteria this has not been an issue.

  - NERC has posted standards for Facility Ratings and Transmission Security Limits,  with comments due August 29. The comment period was extended to 60 days.

  - Operations is no longer calculating daily limits for non-CSC elements, so proposed monitoring of non-CSC flows for post contingency will have to be modified.

- NERC Compliance program for 2003

  - Self certification for TO’s will be mailed later this summer, due in the Fall.  Compliance will conduct more site reviews on issues than previous years. QSE visits also starting, to review emergency plans, real time data and other issues.

- Event Investigations -  Still reviewing UFLS operation data from the May 15th event.  Many UF relays did not operate based on what we are getting initially; asking SPWG chair to get additional fault recorder or other device frequency records to validate ERCOT’s recording.

- Resource Plan Performance Metrics – Compliance working with QSEPM’s and ERCOT Mkt Operations on a pilot measure of resource plan accuracy.   TAC/PUCT has made this a priority item.  Status report filed with PUCT on August 1.

- Compliance will be contacting all generators who have not completed reactive tests since the start of the new market in August.  Test reports have been pouring in.