ERCOT Operations Report

ROS & OWG

August 2003

Frequency control issues (High or Low Frequency) 59.9 > F > 60.1

| Time | Frequency | Event |
| --- | --- | --- |
| 8/2/2003 20:03 | 59.883 | Trip: 390 MW |
| 8/6/2003 15:03 | 59.888 | Trip: 480 MW |
| 8/7/2003 9:09 | 59.899 | Trip: 210 MW |
| 8/7/2003 15:21 | 59.899 | 5 units ran back and tripped 15:00 - 15:30: 930 MW |
| 8/8/2003 16:00 | 59.794 | 6 Units Tripped: 842 MW |
| 8/10/2003 1:38 | 59.886 | Trip: 550 MW |
| 8/10/2003 9:58 | 59.898 | 2 Units tripped: 300 MW |
| 8/24/2003 0:15 | 59.885 | 770 MW Unit ran back to 240 MW |
| 8/25/2003 12:52 | 59.845 | Trip: 735 MW |
| 8/28/2003 11:29 | 59.830 | 3 Units Tripped 663 MW |

|  |  |  | Reg | ERCOT | Schedule Change |
| --- | --- | --- | --- | --- | --- |
| Time | Frequency | Load | (Max) | SCE | (Largest QSE Change) |
| 8/9/2003 9:04 | 59.891 | 36973 | -13 | -814 | 1915 (650) |
| 8/9/2003 10:04 | 59.888 | 39497 | -244 | -519 | 1871 (421) |
| 8/10/2003 12:20 | 59.864 | 44100 | -120 | -502 | ** |
| 8/22/2003 22:01 | 59.889 | 40502 | 279 | -679 | -3250 (1540) |
| 8/28/2003 15:05 | 59.897 | 54359 | 845 | -4482 | 885 (315) |
| 8/28/2003 15:42 | 59.897 | 55112 | 850 | -4874 | 106 (76) |
| 8/3/2003 8:30 | 60.103 | 33548 | 336 | 114 | 142 (0) |
| 8/4/2003 8:32 | 60.110 | 37930 | 194 | 209 | 101 (-7) |
| 8/9/2003 9:36 | 60.137 | 38682 | -388 | 629 | 304 (-173) |
| 8/10/2003 9:34 | 60.112 | 34808 | 210 | 643 | 88 (0) |
| 8/10/2003 11:36 | 60.121 | 42001 | -72 | 638 | ** |
| 8/11/2003 15:31 | 60.110 | 51024 | -545 | 791 | 120 (-1) |
| 8/12/2003 0:04 | 60.109 | 32097 | 239 | 627 | 1875 (1306) |
| 8/12/2003 8:59 | 60.104 | 34144 | 252 | -450 | 717 (-63) |
| 8/13/2003 0:05 | 60.107 | 31498 | -211 | 2398 | -2846 (-1231) |
| 8/18/2003 3:19 | 60.105 | 32162 | 52 | 514 | 258 (-1) |
| 8/18/2003 21:25 | 60.108 | 49109 | -1380 | 386 | -567 (-329) |
| 8/26/2003 10:50 | 60.113 | 43534 | -490 | 342 | 306 (0) |
| 8/29/2003 22:08 | 60.159 | 43872 | -639 | 756 | -3908 (-1340) |

**  Suspect Telemetry and incorrect STLF values over this hour.

Locations and Relative Activity of Congestion Management

Occurrences for August of 2 days or less, listed below:

Argyle – Corinth					PH Robinson T1

Asherton – Eagle Pass					Raymondville 2 Auto

Bates Auto						Roanoke – Euless

Bates – Garza					Sherman Line Materials – Whitesboro

Coleto Creek – Victoria				Spunky - Hood

Collin – Arco T					Valley - Collin

Collin – Everman					Valley - Farmersville

Everman Sw – Oak Hill Tap				Venus - Everman

FT Lancaster – ILL					Venus-Webb-Cedarhill

GarlandRd – PlanoRd					Wedgewood - Rockcreek

Kendal Auto						West - North

Kennedy Sw						Whitepoint – Nueces Bay

Midland – Odessa					Zorn - Hayes

Mountain Creek – Cedarhill				Zorn – Lytton/Austrop

N Edin – RioHondo

N McCallen – McCall

*Days of units purchased for some time in the area described.  Data taken from daily reports and is approximate.  For global overview purposes only.

** No additional congestion management in wind farm area

New Procedures/ Forms/ Operations Bulletins

| 08/11/2002 | ERCOT Market Operations Bulletin 12 |  | Settlement of Mismatched Inter-QSE Energy Schedules after Implementation of PRR387 |
| --- | --- | --- | --- |
| 08/27/2003 | ERCOT Power Operations Bulletin 33 | Revised the Forced/Level 1 Outage Information Sheet |  |
| 08/27/2003 | ERCOT Power Operations Bulletin 32 | Actual Start & End Entries -- Outage Scheduler Enhancements |  |

# Security Alert Stage/ Threatcon/ Related issues

Security Threat Alert Yellow (Elevated) maintained through August.

OCN, Advisory, Alert, Energy Notice and Major Events

| LOG DATE | START | END | LOG TYPE | COMMENTS |
| --- | --- | --- | --- | --- |
| 8/3/2003 | 13:25 | 20:00 | OCN | Issued for North to Houston. |
| 8/4/2003 | 2:17 | 0:00 | OCN | Issued for North to Houston. |
| 8/5/2003 | 6:47 | 0:00 | OCN | Issued for North to Houston. |
| 8/5/2003 | 8:17 | 0:00 | OCN | Issued for North to Houston. |
| 8/8/2003 | 6:38 | 0:00 | OCN | Issued for North to Houston. |
| 8/8/2003 | 15:04 | 0:00 | Alert | Issued for Lapeno - Falcon above 1st contingency limit. |
| 8/8/2003 | 15:06 | 0:00 | Alert | Issued for Laredo Import above 1st contingency limit. |
| 8/9/2003 | 0:00 | 3:30 | Alert | Issued for Lapeno - Falcon above 1st contingency limit. |
| 8/9/2003 | 9:30 | 23:59 | OCN | Issued for North to Houston. |
| 8/9/2003 | 14:00 | 23:59 | Alert | Issued for Rio Hondo - La Palma above 1st contingency limit. |
| 8/9/2003 | 18:00 | 23:59 | Alert | Issued for Lapeno - Falcon above 1st contingency limit. |
| 8/15/2003 | 11:54 | 0:00 | OCN | Issued for Rio Hondo - La Palma expeced to exceed 1st contingency limit. |
| 8/15/2003 | 12:19 | 0:00 | Alert | Issued for Lake Creek - Jewett above 1st contingency limit. |
| 8/15/2003 | 15:35 | 0:00 | Alert | Issued for Lapeno - Falcon above 1st contingency limit. |
| 8/16/2003 | 9:00 | 0:00 | OCN | Issued for North - Houston. |
| 8/17/2003 | 15:57 | 0:00 | Alert | The following Alerts were issued at 13:45: Navarro to Richland and Lapeno to Falcon. |
| 8/18/2003 | 5:45 | 0:00 | OCN | Issued for North to Houston. |
| 8/18/2003 | 9:25 | 10:56 | Alert | Issued for Navarro - Richland above 1st contingency limit. |
| 8/19/2003 | 6:17 | 0:00 | OCN | Issued for North to Houston. |
| 8/21/2003 | 3:17 | 0:00 | Advisory | Issued for the loss of the 345/138KV Autotransformer at W. Denton. |
| 8/26/2003 | 16:31 | 0:00 | Alert | Issued for Lapeno - Falcon above 1st contingency limit. |
| 8/31/2003 | 4:00 | 0:00 | OCN | Wet weather in coastal region |

Significant Communication Problems

8/25  11:45 – 12:45   Deployments not  sent while the portal was inoperable.

Major Computer Systems Problems/ Fixes

8/10  18:30 – 20:15   Three of the four operating desks lost MOI and POS due to a bad

cable.

Major system Voltage problems

8/8   138 kV system  experienced voltage levels below .93 pu briefly following a loss of

multiple transmission lines .

Blackout/Load Shed incidents

8/7  Approximately 375 MW lost due to multiple line trips.

8/7 16:35   465 MW Laars deployed

8/8  356 MW Laars deployed following  a disturbance.

ERCOT peak for last month (Unofficial)

8/7 17:00 60157 (unofficial)

Update on New Generation

None

Max Temperature

8/9  109.5 F in the Far West.

# New SPS & RAP’s

8/6    RAP implemented for Zorn AT1 for loss of Ferguson (required during Zorn

AT2 outage).

8/20  RAP created to control 138 loading in the Denton County area during the

West Denton 345/138 outage.