Northeast ERCOT Congestion Study Report

(09/23/03)

Purpose

CMWG requested that a study be done to investigate and determine if viable and acceptable options exist that could be implemented to reduce Northeast ERCOT congestion in 2004.

Study Scope

This study examined only options to congestion that could be implemented by the 2004 summer peak.    Specifically it examined the use of additional SPSs, system configuration changes, and possible switchable 138 kV series reactors.   The study used the 2004 summer peak base case recently completed.    This study:

- Determined possible overloads and associated contingencies that could occur on the Northeast ERCOT transmission system, as it is presently planned for the summer of 2004.

- Determined acceptable mitigating options (specific SPSs, system configuration changes, 138 kV series reactors) that could be implemented by summer of 2004.

- Assumed acceptable mitigating options were implemented, and determined:

  - Remaining overloads and associated contingencies.

  - Lines to monitor and associated flow limits necessary to eliminate all remaining overloads.

- Determined modifications, if any, that may be necessary to properly interface proposed mitigating options with existing SPSs.

- Assessed the system impact of each proposed SPS’s

  - Failure to operate, and

  - Misoperation

- Determined a rough implementation schedule for proposed mitigating options.

Study Assumptions

The following assumptions were made for this study:

- The 2004 summer peak case dated 7/24/03 was used for this study.

- Known corrections and the latest transmission plans that would have an impact on the study were reflected in the study case.  Case changes made were as follows(double click on icon to open):

- The Anna – Collin 345 kV line rating was shown incorrectly in the above imbedded document.   The correct rating is 1370 MVA rather than 1434 MVA and is reflected in the study results.

- The West Denton 345/138 kV autotransformer would be replaced by the 2004 summer peak.  (The autotransformer out condition will be studied only if there are strong indications that the autotransformer will not be replaced by then, and only to test its impact on proposed mitigating options.)

- A 345 kV breaker would be installed at Allen Switching Station to insulate the Allen Autotransformer from line outages.

- Generation assumptions were as follows: (double click on icon to open)

- The only mitigating options to be considered were:

  - SPSs

  - 138 kV series reactors (switched only)

  - System configuration changes(lines operated normally open, etc.)

Study Results

AC Contingency Calculation (ACCC) runs were made on the above study case.    The results are shown in Appendix A.    There were approximately 139 contingencies resulting in 322 occasions where facilities were loaded to 100 % or more.   These results were then filtered to remove contingencies and overloads that were not related to the amount of generation on line in Northeast ERCOT.    The resulting table is shown in Appendix B.  After filtering there were 37 contingencies resulting in 94 occasions where facilities were loaded to 100% or more.    The effects of existing series reactors and SPSs were checked against each remaining contingency.   Possible mitigating options to remove remaining overloads were then explored for each contingency.   A table of the contingency overloads with solutions is shown in Appendix C.   The proposed solutions include SPSs, automatic remote tripping of breakers, changes in the normal state of breakers and switches, Contingency Response Plans (CRPs), and modifications to system improvements underway.   The following solutions were found to be effective in addressing the overloads:

SPSs –

- Modify the existing Valley SPS and incorporate remote monitoring (at Anna) of the Anna – Collin 345 kV line, the Anna – Chambersville 138 kV line and the Anna Sw. Sta. 345/138 kV autotransformer.  The Valley – Farmersville 345 kV line will also be monitored.   Overloads on these facilities will result in sequential tripping of the first train at Kiamichi, Valley #3 and the second train at Kiamichi as needed to relieve the monitored overloads.

- Install a new SPS on the Valley 138 kV generation.   The Valley – Payne #1 and Valley – Payne #2 138 kV lines will be monitored.   Valley #2 generation will be runback and tripped if necessary to relieve overloads

- Install automatic breaker tripping on the Valley – Payne #2 138 kV  line (brkr. # 3380) for overloads on the Valley 345/138 kV autotransformer.  This is being done to avoid/minimize generation tripping for overloading of the autotransformer.

- Install automatic remote breaker tripping at Collin.   The Collin – Bridges line will be monitored.   The remote end of this line will be tripped when it overloads.

- Install automatic breaker tripping at E. Mesquite on the line to W. Mesquite.  Both E. Mesquite to Forney circuits will be monitored for overloads for this automatic tripping.

- Modify the existing Monticello thermal SPS and incorporate remote monitoring (at Farmersville) of the Farmersville – Royse #1 and Farmersville – Royse #2 345 kV circuits.   The Monticello – Sulphur Springs, Monticello – Allen, and Monticello – Farmersville #1 345 kV circuits will also be monitored.    Overloads on any of these facilities will result in the DC tie being tripped.

System configuration changes –

- Operate with E. Richardson Brkr. #3400 normally open.   This will address overloads as high as 140 % on the Rockwall – Garland 138 kV line section for loss of the double circuit 345 kV line between Royse and Allen.

- Operate with 69 kV Switch #906 normally closed at Cooper.   This will eliminate 138 kV overloads that occur on the line from Valley to Commerce.

- Operate with 138 kV Switch # 380 normally open at NW Sherman.   This will eliminate overloads on the North Denison – Denison Dam Tap line section.

CRPs –

- Contingency outage of the Forney – Centerville 345 kV line will result in the Royse – Ben Davis 345 kV line overloading (< 110%).   Opening 138 kV Brkr. #042 at Centerville Switch will result in the series reactor on the Centerville – Garland Rd. #2 circuit automatically switching in.   The combination of these two actions will increase the impedance to area loads sufficiently to eliminate the overload.

- Contingency overloads on the Terrel N. Tap – Terrel North 138 kV line section that are caused by flow through can be relieved by closing 69 kV switch #733 and opening 69 kV switch #732 at Wills Point, shifting this load to Edgewood.    Overloads caused by connected load in the absence of any flow through, do not impact congestion.

Modification of system improvements now underway –

- Increase the size of the series reactor planned for the Allen autotransformer from two ohms to three ohms.

- Rebuild and install one circuit of 1590 ACSR (326 MVA) from Custer to Rolater to Lebanon before the summer of 04.

- Release the Northaven – Alpha Rd. 138 kV line for elevated temperature operation (120 degrees C for 274 MVA) before it is rebuilt.   Recently completed design research necessary for the rebuild provided the information to allow the decision to be made on elevated temperature operation.   Replace existing wave trap early to remove equipment limitations.

It is felt that the above SPSs can be implemented, with redundant communication links (power line carrier and a dedicated leased phone circuit) and with SPS arming for loss of both communication links, such that there will be minimal impacts on transmission reliability.  The Monticello SPS will be set to arm and activate before the Valley 345 kV and existing Paris SPSs are armed.   The Paris SPS arming delay time will be extended to help accomplish this.  This should minimize the reduction in generation necessary to address the overloads.   Rationale for interrupting the DC tie first is the fact that it can be brought back much quicker than a tripped generator.   The above change in the Paris SPS represents the extent of the changes necessary to interface existing SPSs with the new and modified SPS proposals contained here.   See Appendix D for more details on the proposed SPSs.   The second CRP above had been previously identified for summer operations.   Both CRPs are fairly simple operations that can be implemented quickly.

The impacts of SPS failure and SPS mis-operation were investigated as the last step of this study.   Loss of the double circuit 345 kV line between Allen and Royse with the dispatch studied would result in the Anna – Collin 345 kV line loading in excess of 120%.   Subsequent tripping of this circuit would result in cascading outages in the northeast – north interface that could result in voltage collapse in the Dallas area.   This could be avoided if operator action to open the Valley – Kiowa line was timely.   Loss of the double circuit 345 kV line between Farmersville and Royse would result in the Anna – Collin 345 kV line loading to 129 %.   The Monticello SPS and Valley 345 kV SPS would both be involved here.   Failure of the Monticello SPS would not be detrimental in this case.   Failure of the Valley 345 kV SPS would result in the Anna - Collin 345 kV line being loaded to 113 %.  This loading would be more likely to allow the operator time to trip the Valley – Kiowa 345 kV line and should be manageable.   Loss of the Anna – Collin 345 kV line results in the Anna – Chambersville 138 kV line loading to 126 %.   Failure of the Valley 345 kV SPS and subsequent tripping of this line will result in the Monticello and the Valley 138 kV SPSs being activated.   These SPSs will eliminate any remaining overloads.   Loss of the Valley – Anna 345 kV line will result in the Valley – Farmersville 345 kV line loading to 123 %.  Failure of the Valley 345 kV SPS and subsequent tripping of this line could result in damage to Valley 345/138 kV autotransformer (170 % loading) and loss of both the Kiamichi and Lamar generation.   Here again, timely opening of the Valley – Kiowa 345 kV line could eliminate all overloads.   For the generation dispatch studied, no other contingencies resulted in 345 kV line overloads that exceeded 120 %.   SPS failures in those situations should be manageable.   SPS mis-operation should not be damaging to the system.  Mis-operation could result in as much as 1550 MVA of generation being tripped unnecessarily.   However, staging of the generation tripped should avoid any stability issues.

Summary

Implementation of the above proposed solutions should eliminate congestion under pre-contingency conditions for the 5060 MW of generation modeled in the study with a 600 MW import over the East HVDC tie in northeast ERCOT.   No flow limits were determined to be necessary with the study dispatch and the proposed solutions.    It appears that implementation can be accomplished by the summer of 2004.   The longest lead time (as long as 6 months) may be in obtaining dedicated leased phone circuits.   It is guesstimated that the SPSs can be implemented for less than $1,000,000.   The other identified improvement modifications will result in negligible cost increases over what was already underway.   The above study results are based on the assumption that a number of planned system improvements will be completed by the 04 summer, as scheduled.   Since most of these improvements involve upgrades of existing facilities, it is likely that needed clearances will result in even more congestion in the interim.   Refusal to grant clearances will make it impossible to meet schedules and have the necessary facilities in place by the summer of 04.

Appendices

(Double click on icon to open document)

| Appendix A |  | ACCC run results for the 2004 summer peak study case with monitor and contingency files included. |
| --- | --- | --- |
| Appendix B |  | ACCC run results filtered to remove contingencies and overloads that do not impact the northeast congestion. Contingency descriptions are included. |
| Appendix C |  | Solutions identified for each overload shown in the filtered run results. |
| Appendix D |  | Conceptual descriptions of the proposed SPSs. |