## ERCOT Operations Report

## ROS & OWG

## September 2003

September-Frequency control issues (High or Low Frequency) 59.9 > F > 60.1

|  |  |  | Reg | ERCOT | Schedule Change |
| --- | --- | --- | --- | --- | --- |
| Time | Frequency | Load | (Max) | SCE | (Largest QSE Change) |
| 9/4/2003 5:55 | 60.108 | 30437 | -93 | 727 | 2975 (1000) |
| 9/8/2003 8:50 | 60.115 | 32447 | -837 | 687 | 1375 (330) |
| 9/9/2003 8:59 | 59.883 | 33817 | -76 | -87 | 1375 (585) |
| 9/9/2003 14:07 | 59.896 | 46680 | 510 | -914 | 1150 (450) |
| 9/10/2003 14:23 | 60.121 | 48427 | -28 | -219 | 450 (300) |
| 9/16/2003 0:01 | 60.123 | 29585 | 184 | 881 | -875 (-175) |
| 9/19/2003 5:58 | 60.103 | 26637 | -1090 | 577 | 2550 (750) |
| 9/19/2003 6:08 | 59.879 | 27289 | -381 | -1640 | 2550 (750) |
| 9/19/2003 22:01 | 59.874 | 32522 | -390 | -1382 | - 3800 (-1475) |
| 9/19/2003 22:34 | 59.889 | 31399 | 461 | -765 | -1150 (-550) |
| 9/21/2003 22:14 | 60.113 | 31229 | 233 | 40 | -550 (-225) |
| 9/22/2003 5:31 | 60.122 | 25644 | -244 | 760 | 1250 (950) |
| 9/22/2003 22:05 | 59.876 | 34647 | 28 | -2047 | -4150 ( -1550) |
| 9/22/2003 22:13 | 60.111 | 34300 | -46 | -292 | -4150 ( -1550) |
| 9/23/2003 0:35 | 60.114 | 26903 | -1230 | 584 | -525 (-250) |
| 9/24/2003 22:10 | 60.104 | 35680 | 110 | 259 | -4075 (-1850) |
| 9/25/2003 6:05 | 59.868 | 28539 | -17 | -680 | 2750 (950) |
| 9/25/2003 12:01 | 60.108 | 39158 | 141 | -1413 | 1000 (575) |
| 9/25/2003 22:04 | 59.856 | 36091 | 860 | -2071 | -4050 (-1575) |
| 9/25/2003 22:14 | 60.133 | 35647 | 481 | -108 | -4050 (-1575) |
| 9/29/2003 6:12 | 59.898 | 25946 | -437 | -603 | 2325 (850) |

| Time | Frequency | Resource lost |
| --- | --- | --- |
| 9/1/2003 14:02 | 59.882 | 500 MW unit trip |
| 9/8/2003 6:04 | 59.888 | Ct and steam unit trip during ramp period. |
| 9/10/2003 12:29 | 59.827 | 540 MW unit trip |
| 9/11/2003 9:22 | 59.817 | 620 MW unit trip |
| 9/13/2003 9:45 | 59.890 | 345 MW Ct and steam unit trip. |
| 9/16/2003 13:41 | 59.899 | 625 MW at station tripped. |

September-Locations and Relative Activity of Congestion Management

Occurrences for September of 3 days or less, listed below:

Allen Sw – Royse Sw – MNSES			N Edin – Rio Hondo

Asherton – Eagle Pass					N McCallen - McCall

Austrop Auto						Polk – Hall Acres

Bates – Garza						Rio Grand/La Grulla

Clearsprings – Zorn – Marion				Shamburger - Elkton

Everman SW – Oak Hill Tap				Spunky - Hood

Tricorner - Watermill 					Killeen – Copperas Cove

Garza – Roma						Whitepoint – Nueces Bay

*Days of units purchased for some time in the area described.  Data taken from daily reports and is approximate.  For global overview purposes only.

New Procedures/ Forms/ Operations Bulletins

| 09/30/2003 | ERCOT Power Operations Bulletin 40 | Revision to the Transmission & Security Desk Procedures |
| --- | --- | --- |
| 09/30/2003 | ERCOT Power Operations Bulletin 39 | Revision of the Operating Period Desk Procedures |
| 09/30/2003 | ERCOT Power Operations Bulletin 38 | Revision of Frequency Control Desk Procedures |
| 09/30/2003 | ERCOT Power Operations Bulletin 37 | Revision of Day-Ahead Desk Procedures |
| 09/30/2003 | ERCOT Power Operations Bulletin 36 | Revision of Direct Current Ties Procedures |
| 09/16/2003 | ERCOT Power Operations Bulletin 35 | Procedure when OOMEing Combined Cycle Units Off Line |
| 09/04/2003 | ERCOT Power Operations Bulletin 34 | Revision of Operating Procedures |
| 09/04/2003 | Shift Supervisor V2R0 | Update to current practices after additional operator reviews. |
| 9/29/2003 | Day-Ahead Desk V2R9 | Update to current practices after additional operator reviews. |
| 9/29/2003 | Direct Current Ties V1R3 | Update to current practices after additional operator reviews. |
| 09/29/2003 | Frequency Control Desk V2R7 | Update to current practices after additional operator reviews. |
| 09/29/2003 | Operating Period Desk V2R5 | Update to current practices after additional operator reviews. |
| 09/29/2003 | Transmission & Security Desk V2R11 | Update to current practices after additional operator reviews. |

# Security Alert Stage/ Threatcon/ Related issues

Security Threat Alert Yellow (Elevated) maintained through August.

OCN, Advisory, Alert, Energy Notice and Major Events

| LOG DATE | START | END | LOG TYPE | COMMENTS |
| --- | --- | --- | --- | --- |
| 9/1 | 04:00 | 14:45 | OCN | Weather in the Costal area. |
| 9/1 | 10:13 | 23:05 | OCN | Issued for North to Houston. |
| 9/2 | 10:30 | 12:15 | OCN | Issued for North to Houston. |
| 9/3 | 06:15 | 11:30 | OCN | Issued for North to Houston. |
| 9/4 | 06:30 | 12:15 | OCN | Issued for North to Houston. |
| 9/5 | 06:50 | 12:00 | OCN | Issued for North to Houston. |
| 9/6 | 15:55 | 23:59 | Alert | Falcon – Lapeno above 1st contingency limit. |
| 9/10 | 06:11 | 22:00 | OCN | Issued for North to Houston. |
| 9/11 | 11:10 | 12:45 | OCN | Issued for North to Houston. |
| 9/14 | 10:10 | 19:45 | OCN | Issued for North to Houston. |
| 9/18 | 11:14 | 22:00 | Alert | Spunky – Hood above 1st contingency limit. |
| 9/19 | 11:00 | 22:00 | OCN | Issued for North to Houston. |
| 9/25 | 15:27 | 22:45 | Alert | Issued for Nacogdoches 1170_A/Shamburger 1775_A above 1st contingency limit. |

Significant Communication Problems

09/06 18:00 - Deployments not sent while the portal was inoperable.

09/9  13:00 – 13:30	Market extended due to portal problems.

09/9   13:15 – 14:00	Held intervals due to MOS problems.

## Major Computer Systems Problems/ Fixes

09/05 15:48 –Failover executed to correct data acquisition problem.

09/10 22:08 – 22:40 – POS at ACC is not responding.

09/30  19:00 – 22:00  ERCOT backup center down.

# Major system Voltage problems

None

Blackout/Load Shed incidents

None

ERCOT peak for last month (Unofficial)

9/9 17:00 49,564 (unofficial)

## Update on New Generation

None

## Max Temperature

9/9 & 9/10  97.0 F in the Far West.

# New SPS & RAP’s

None

# Other

9/7  (Sunday) 09:30 – 16:00  ERCOT Austin control center primary site.