Competitive Metering
Guides

November 6, 2003 [DRAFT with comments]

The document needs to be checked for the consistent use of terms.

In the event of any conflict for parties that are operating in the ERCOT Region between these Guides and state law, PUCT rules, or the ERCOT Protocols, such conflict shall be resolved in favor of the applicable law, rules, or Protocols.  Should these Guides become applicable for any parties operating within the state of Texas, but outside of the ERCOT Region, such conflict shall be resolved in favor of the applicable law or rules in effect in that region.

The entity or the documents that will resolve the boxed language are identified by the following color code:

RMS

Final Terms & Conditions

Final Agreement

1	Purpose and Scope	4

1.1	Competitive Metering Guides (CMG)	4

1.2	Competitive Metering Working Group (COMETWG)	4

2	Roles and Responsibilities of Market Participants	6

2.1	Customer	6

2.2	Competitive Retailer (CR) associated with an Electric Service Identifier (ESI ID)	7

2.3	Meter Owner	7

2.4	Transmission and/or Distribution Service Provider (TDSP)	7

2.5	Electric Reliability Council of Texas (ERCOT)	8

2.6	Public Utility Commission of Texas (PUCT)	8

3	Competitively Owned Meter Installation overview	8

4	Meter Information Requests	9

4.1	Initial Inquiry	9

4.2	TDSP Response	9

5	Meter Selection	10

6	Programming Specifications for Solid state devices	10

6.1	Customer Programming Specifications	10

6.2	Number of Interval Data Recorder (IDR) Channels to Program into a Meter	11

6.3	TDSP Tariff Billing and ERCOT Settlement Determinants	12

6.4	CR Billing Requirements	12

6.5	Other Programming Requirements	12

7	Installation of a Competitively Owned Meter	12

7.1	Existing Service with TDSP Meter Installed	12

7.2	New Service (Construction) with No Meter Installed	14

7.3	Notification Requirements	17

7.4	One ESI ID with Multiple Meters	18

8	Meter Testing and Calibration	19

8.1	Accuracy Limits	19

8.2	Test Schedules	19

8.3	Meter Records	19

8.4	TDSP Calibration	19

8.5	Notification Requirements	19

9	Removal of a Competitively Owned Meter	20

9.1	Move Outs	20

9.2	Replacing Defective Equipment	21

9.3	Notification Requirements	21

9.4	Customer Requests to Return to TDSP Owned Meter	22

9.5	Safeguarding Meters	22

10	Customer or Third Party Access to the Meter	22

10.1	Data Access	22

10.2	Passwords	23

10.3	Meter Communication Responsibilities	23

10.4	Physical Access	23

11	TDSP billing and Credits per TDSP Approved Tariff	24

11.1	TDSP Approved Credits	24

11.2	TDSP Approved Tariffs	24

11.3	TDSP Approved Metering Service Credits and Tariffs	24

12	Technical Specifications for Competitively Owned Meters	24

12.1	Purpose	24

12.2	ANSI Standards	24

12.3	TDSP Tariff Billing Determinants	25

12.4	Transformer and Line Loss Compensation – Optional Functionality	25

12.5	Display	25

12.6	Meter Diagnostics for Solid State Poly-phase Meters	26

12.7	Solid State Display Modes	26

12.8	Power-up Operation	26

12.9	Nameplate and Identifiers	27

12.10	Self-Test	27

12.11	Diagnostic Checks	27

12.12	IDR Pulse Overrun	27

12.13	Event Logging	27

12.14	Error Reset	28

12.15	Communication	28

12.16	Accuracy Standard	28

12.17	Interval Data Recorder (IDR) Functionality	29

12.18	Internal Clock	29

12.19	Outage Carryover	29

12.20	Meter Password	29

12.21	Reliability	30

12.22	Field Requirements	30

12.23	Shop Requirements	30

13	Meter Approval Process	30

14	Meter Firmware/Functionality Changes for an Approved Meter	32

15	Meter Issue Resolution Process	33

16	Meter Ownership Transfer	35

16.1	Introduction	35

16.2	Communication Process	35

17	Competitive Metering Guides Change Control Process	35

17.1	Overview	35

17.2	Roles and Responsibilities	36

18	Metering Forms	42

18.1	Forms Posted on the ERCOT Web Site	42

18.2	Form Revision	42

# Purpose and Scope

## Competitive Metering Guides (CMG)

### Purpose

The purpose of the CMG is to define standards, specifications, procedures and practices for competitively owned meters.  In addition, these Guides will add details required to clarify the language in the ERCOT Protocols that affect competitive metering.

### Scope

The scope of the CMG is limited to competitively owned meters and to practices associated with competitive meter ownership.

### General Information

Specific practices described in the CMG are consistent with the Public Utility Commission of Texas (PUCT) Substantive Rules and the ERCOT Protocols.  In the event of any conflict for parties that are operating in the ERCOT Region between these Guides and state law, PUCT rules, or the ERCOT Protocols, such conflict shall be resolved in favor of the applicable law, rules, or Protocols.  Should these Guides become applicable for any parties operating within the state of Texas, but outside of the ERCOT Region, such conflict shall be resolved in favor of the applicable law or rules in effect in that region.

For requirements of other metering applications, refer to the appropriate section of the ERCOT Protocols.

### Definitions

Terms used in the CMG are defined in Section 2 of the ERCOT Protocols unless specifically defined in the CMG.  The term TDSP, when used in the CMG, refers to TDSP service territories where competitive meter ownership is authorized.

## Competitive Metering Working Group (COMETWG)

### Purpose

The COMETWG is a standing informal, open working group that provides technical support to the Retail Market Subcommittee (RMS) on competitive metering issues.

The COMETWG provides a forum in which Market Participants and other interested parties may participate to facilitate changes in standards, specifications, procedures and practices associated with competitive metering as reflected in the Protocols and the CMG.

### Scope

The COMETWG, as directed by RMS, shall be involved in policy issues and operational aspects of competitive metering.

### Roles and Responsibilities

The COMETWG roles and responsibilities include but are not limited to:

- Making recommendations to maintain and uphold Protocols as they pertain to competitive metering;

- Developing and maintaining the CMG;

- Reviewing and processing all requests for changes to the CMG;

- Reviewing and establishing recommendations for submittal to RMS regarding necessary business policies and procedures that affect competitive metering;

- Participating in developing business requirements for any transaction changes necessary to implement PUCT approved rules related to competitive metering and delivering said requirements to Texas Standard Electronic Transactions Working Group (TX SET) and the Texas Test Plan Team (TTPT);

- Performing a liaison function between Market Participants and ERCOT and facilitating market acceptance of competitive metering processes; and,

- Providing a forum for Market Participants to be involved with competitive metering.

### Structure and Leadership Responsibilities

The COMETWG reports to RMS, which is a standing subcommittee of the Technical Advisory Committee (TAC).

The COMETWG Chair and COMETWG Vice Chair are elected annually by the COMETWG on a calendar year basis and the names are submitted to RMS for approval.

The Chair leads the COMETWG meetings, establishes COMETWG meeting schedules, ensures meeting minutes are documented and distributed, and represents the COMETWG at RMS and other ERCOT forums, as necessary.

The Chair can establish task forces and/or sub teams to facilitate the COMETWG objectives and timelines.

The Vice Chair’s primary responsibilities are to assist the Chair in performance of the Chair’s duties and perform the Chair’s duties in the absence of the Chair.

### Membership and Meetings

The COMETWG membership and meetings are open to all Market Participants and any other interested parties.

### COMETWG Distribution List

To receive electronic mail (e-mail) related to the COMETWG, complete the following process:

- Through your web browser go to http://lists.ercot.com

- Enter your e-mail address in the first box.

- Select the “Find” button and type “cometwg” into the open box next to the find button.

- Click on the “Go” button.  A new page with the “cometwg” list will appear.

- Place a check mark in the “Sub” box next to the “cometwg” list.

- Click on the “Apply” button.

To stop receiving electronic mail (e-mail) related to the COMETWG, complete the following process:

- Through your web browser go to http://lists.ercot.com

- Enter your e-mail address in the first box.

- Select the “Find” button and type “cometwg” into the open box next to the find button.

- Click on the “Go” button.  A new page with the “cometwg” list will appear.

- Remove the check mark in the “Sub” box next to the “cometwg” list.

- Click on the “Apply” button.

# Roles and Responsibilities of Market Participants

The roles and responsibilities of Market Participants as they relate to competitive meter ownership are described in this section.

## Customer

Customer roles and responsibilities include but are not limited to:

- Choosing whether to own or authorize a third party (Customer’s agent) to own a competitive meter for their Electric Service Identifier (ESI ID);

- Entering into an Agreement for Meter Ownership and/or Access (Agreement) with the TDSP for a competitively owned meter;

- Choosing whether to delegate their competitive meter ownership responsibilities to another Entity;

- Initiating the process to have meters added to the Qualified Competitive Meter List posted on the ERCOT web site;

- Providing a meter to the TDSP that is on the Qualified Competitive Meter List ;

- Submitting the Texas Meter Information (TMI) Form requesting meter information for the ESI ID that qualifies for competitive meter ownership;

- Requesting installation and/or removal of a competitively owned meter; and,

- Charges for construction services that the Customer or Customer’s agent requests in accordance with the TDSP approved tariffs.

Review 2 upon Agreement being finalized.  Update applicable areas when final determination is made. (Customer, CR, meter owner).

## Competitive Retailer (CR) associated with an Electric Service Identifier (ESI ID)

CR roles and responsibilities include but are not limited to:

- Initiating a meter test request to the TDSP on behalf of the Customer;

- Charges for services provided in accordance with the TDSP approved tariffs; and,

- Upon agreement with the Customer or Customer’s agent, requesting installation and/or removal of a competitively owned meter.

  - Competitive Meter Owner

Competitive meter owner roles and responsibilities include but are not limited to:

- Perform competitive meter ownership duties authorized by the Customer.

Will the meter owner be responsible for signing a legal agreement with the TDSP for installation and maintenance of a competitively owned meter?  Review upon terms & conditions being finalized.  Update applicable areas when final determination is made. (Customer, CR, meter owner).

Should roles and responsibilities be added for a meter access agent?

## Transmission and/or Distribution Service Provider (TDSP)

TDSP roles and responsibilities include but are not limited to:

- Providing metering services relating to installation and removal, maintenance, testing and calibration, data collection and data management as required for TDSP billing and settlement, including the transfer of meter data to the settlement agent;

- Security of the data used for settlement and TDSP billing and maintaining the meter programming password capable of altering such billing parameters;

- Making recommendations for approval or removal of meters on the Qualified Competitive Meter List in accordance with these CMG;

- Completion of “TDSP” sections of the TMI and the Texas Meter Access (TMA) forms in response to inquiries submitted per the requirements specified in these CMG;

- Providing a competitive metering service credit to the CR of a Customer that selects a meter owner other than the TDSP per PUCT approved tariffs;

- Safeguarding a competitively owned meter per these CMG; and,

- Signing an Agreement with the Customer for installation and maintenance of a competitively owned meter.

Number 7 – Will the TDSP be responsible for signing a legal agreement with the meter owner for installation and maintenance of a competitively owned meter?  Update applicable areas when final determination is made. (Customer, CR, meter owner).

## Electric Reliability Council of Texas (ERCOT)

ERCOT roles and responsibilities include but are not limited to:

- Processing the required forms in accordance with these CMG;

- Maintaining the Qualified Competitive Meter List posted on the ERCOT web site in accordance with these CMG; and,

- Maintaining the ERCOT Competitive Metering web page.

## Public Utility Commission of Texas (PUCT)

PUCT roles and responsibilities include but are not limited to:

- Providing general oversight of the competitive metering market; and,

- Ultimately handling dispute resolution for competitive metering.

# Competitively Owned Meter Installation overview

The following is a checklist for installation of a competitively owned meter:

- Request meter information for an existing ESI ID or new Premise (see Section 4)

- Select a meter (see Section 5)

- Execute the Agreement with the TDSP (see Section 7.3)

- Provide the meter and programming specifications to the TDSP (see Section 6)

- TDSP installs competitively owned meter (see Section 7)

Meter Information Requests

The purpose of the meter information request is to provide the Customer or Customer’s agent with the minimum requirements that a competitively owned meter(s) must satisfy for each specific metering point at an existing ESI ID or new Premise.  This is a manual process using a market approved standardized form known as the Texas Meter Information (TMI) Form.

## Initial Inquiry

The Customer or Customer’s agent completes the “Contact Information” section of the TMI Form and submits the form, via e-mail, to the TDSP contact. The TMI Form and a link to each TDSP’s competitive metering contact are located on the Competitive Metering page of the ERCOT web site:

Go to www.ercot.com

Select the “Market Participants & Stakeholders” tab

Select “Competitive Metering”

A signed Letter of Authorization (LOA) must accompany the e-mailed TMI Form, if the request is submitted by anyone other than the Customer.

## TDSP Response

Upon receipt of the TMI Form (and LOA if applicable), the TDSP is responsible for the following:

- Completing the “TDSP Information” and “Minimum Meter Replacement Requirements” sections of the form; and

- Returning the form, via e-mail, to the Customer or Customer’s agent within ten (10) Business Days of the date/time stamp on the senders e-mail.

# Meter Selection

The Customer or Customer’s agent is responsible for selecting and purchasing a meter from the Qualified Competitive Meter List that meets the “Minimum Meter Replacement Requirements” section of the TMI Form as completed by the TDSP.  A meter must be on the Qualified Competitive Meter List to be installed as a competitively owned meter.

If a Customer would like to select a meter that is not on the current Qualified Competitive Meter List, see the Meter Approval Process in Section 13.

The Qualified Competitive Meter List is available on the ERCOT website.

# Programming Specifications for Solid state devices

## Customer Programming Specifications

The Customer or Customer’s agent shall provide data requirements to the TDSP for programming a competitively owned meter.

The TDSP will program any competitively owned meter to obtain the appropriate TDSP billing and settlement determinants (TDSP standard program).

The TDSP will customize the meter program to support additional functions as requested by the Customer or Customer’s agent.  If the meter functionality does not allow these items to be programmed separately from TDSP billing determinants, the Customer or Customer’s agent will specify the data and functionality requirements by providing one of the following to the TDSP:

- Check off sheet listing detailed information for functionality requested, including channel designation (manufacturer program printout); or,

- Electronic file generated from the manufacturer’s software.

The TDSP will proceed with the meter installation request unless the Customer or Customer’s agent requests to verify the meter program prior to installation.

If the Customer or Customer’s agent requests to verify the meter program, the request shall be submitted along with the data requirements to the TDSP.  The TDSP will print out the meter program, if the manufacturer’s software supports this functionality, and send the meter program to the Customer or Customer’s agent prior to installing the meter.  The TDSP will continue processing the meter installation request within seven (7) business days after the Customer or the Customer’s agent provides e-mail acceptance of the supplied meter program.

## Number of Interval Data Recorder (IDR) Channels to Program into a Meter

The maximum number of channels that can be programmed into the IDR meter is sixteen (16), which includes TDSP billing and settlement channels.

The minimum number of channels required by the TDSP will be based on the TDSP billing and settlement determinants.

The remaining channels up to the maximum allowable as specified in these CMG are available to the Customer.

The maximum allowable number of IDR channels for a meter may be limited by the requirement to maintain a data storage capacity of 45 days per channel.

The current TDSP billing and settlement intervals are based on a fifteen (15) minute interval.

## TDSP Billing and Settlement Determinants

TDSP billing and settlement determinants are determined by the applicable TDSP tariffs or Affiliated REP Price to Beat (PTB) requirements, for non-IDR only.

Only TDSP billing and settlement data will be sent to ERCOT by the TDSP.

## CR Billing Requirements

The Customer or Customer’s agent must ensure that current CR billing requirements are maintained when requesting competitive meter ownership and supplying programming specifications to the TDSP.

## Other Programming Requirements

TDSP additional requirements other than TDSP billing and settlement determinants for a specific meter will be communicated to the Customer or Customer’s agent during the initial inquiry.

The Customer or Customer’s agent shall, at a minimum, maintain the meter functionality presently installed and necessary to maintain meter reading requirements, safety and reliability of the TDSP’s electrical system.

# Installation of a Competitively Owned Meter

The following section covers the minimum required procedures that must be followed when installing a competitively owned meter, but is not intended to address all contingencies involved with this process.

## Existing Service with Meter Installed

- After receiving the completed TMI Form from the TDSP, via e-mail, the Customer will have sixty (60) calendar days to execute a signed Agreement with the TDSP requesting meter ownership. If the Customer fails to execute the Agreement within the sixty (60) calendar day expiration period for the TMI Form, the Customer or Customer’s agent will be required to restart the process by obtaining and submitting a new TMI Form.

- The current draft agreement shows the Customer as responsible for signing the agreement with the TDSP.

- The Agreement is part of the TDSP tariffs and can be obtained from the ERCOT Competitive Metering web page.

- The Customer or Customer’s agent has the responsibility of shipping the following items, together, to the address specified in the executed Agreement:

- A meter or meters listed on the Qualified Competitive Meter List;

- Data requirements for TDSP programming for each meter; and,

- Completed TMI Form for each ESI ID where meter ownership is being requested. The Customer or Customer’s agent shall specify which existing meter, by serial number, will be replaced by each competitively owned meter, by serial number.

- The TDSP has the responsibility of performing acceptance testing for every meter received, unless the manufacturer’s certified test results are provided and the TDSP accepts such manufacturer’s certified test results.

- If the meter test is acceptable (passed),

- The TDSP shall confirm, via e-mail, to the Customer or Customer’s agent within five (5) Business Days of test acceptance that the meter is ready for installation.

- The Customer or Customer’s agent will confirm site communication readiness with the TDSP, via e-mail.

- Once site readiness has been confirmed, the TDSP will replace the TDSP owned meter with the competitively owned meter.

- If the Customer has executed the “Data Access” section of the Agreement, the TDSP will provide site specific information for the new meter via e-mail on the Texas Meter Access (TMA) Form, within ten (10) Business Days after installation of the competitively owned meter.

- If the meter test is unacceptable (failed),

    - The TDSP will e-mail a completed Meter Test Results / Removal (MTR) Form to the Customer or Customer’s agent within five (5) Business Days of the meter test.

    - The TDSP will return the meter to the meter owner in accordance with instructions provided in the executed Agreement.

    - The Customer or Customer's agent will be responsible for providing a qualified replacement meter, with the appropriate documentation (reference 7.1(3)), within ninety (90) calendar days of the TDSP returning the failed meter or any other agreed upon date between the TDSP and the Customer or Customer’s agent.

    - If a qualified replacement meter has not been received by the TDSP within the ninety (90calendar or business) days, the Customer or Customer’s agent shall reinitiate the process as outlined in Section 3.

## New Service (Construction) with No Meter Installed

The Customer or Customer’s agent is responsible for coordinating the installation of a competitively owned meter with the Customer’s request to energize service. If a competitively owned meter is not available to facilitate the Customer’s request to energize the service the TDSP will install a TDSP owned meter.

- After receiving the completed TMI Form from the TDSP, via e-mail, the Customer will have sixty (60) calendar days to execute a signed Agreement with the TDSP requesting meter ownership. If the Customer fails to execute the Agreement within the sixty (60) calendar day expiration period for the TMI Form, the Customer or Customer’s agent will be required to restart the process by obtaining and submitting a new TMI Form.

- The current draft agreement shows the Customer as responsible for signing the Agreement with the TDSP.  This will need to be reviewed upon finalizing the Agreement.

- If the Customer has provided a letter of authorization to the TDSP authorizing a third party to act on the Customers behalf for meter issues, is the Customer required to sign the Agreement?

- The Agreement is part of the TDSP tariffs and can be obtained from the PUCT web site.

- The Customer or Customer’s agent has the responsibility of shipping the following items, together, to the address specified in the executed Agreement:

- A meter or meters listed on the Qualified Competitive Meter List, forty-five (45) calendar days prior to the requested date for connection of electrical service to the ESI ID;

- Data requirements for TDSP programming for each meter; and

- Completed TMI Form for each ESI ID, if available, or service address where meter ownership is being requested. The Customer or Customer’s agent shall specify the detailed physical location for each competitively owned meter, by serial number.

- The TDSP has the responsibility of performing acceptance testing for every meter received, unless the manufacturer’s certified test results are provided and the TDSP accepts such manufacturer’s certified test results.

- If the meter test is acceptable (passed),

    - The TDSP shall confirm, via e-mail, to the Customer or Customer’s agent within five (5) Business Days of test acceptance that the meter is ready for installation.

    - The Customer or Customer’s agent will confirm site communication readiness with the TDSP, via e-mail.

    - The Customer or Customer’s agent shall notify the TDSP, via e-mail, of the Customer requested move-in date.

    - The TDSP will make all reasonable efforts to schedule the competitively owned meter installation according to the date requested.

    - If the Customer has executed the “Data Access” section of the Agreement, the TDSP will provide site specific information for the new meter via e-mail on the Texas Meter Access (TMA) Form, within ten (10) Business Days after installation of the competitively owned meter.

- If the meter test is unacceptable (failed),

- The TDSP will e-mail a completed MTR Form to the Customer or Customer’s agent within five (5) Business Days of the meter test.

- The TDSP will return the meter to the meter owner in accordance with the instructions provided in the executed Agreement.

- The Customer or Customer's agent will be responsible for providing a qualified replacement meter, with the appropriate documentation (reference 7.2(3)), within ninety (90) calendar days of the TDSP returning the failed meter or a mutually agreed upon date between the TDSP and the Customer or Customer’s agent.

- If a competitively owned meter is not available for the installation, the Customer may choose to cancel the request to energize service through the Customer’s chosen CR (move-in request); otherwise the TDSP will install a TDSP owned meter to comply with the move-in request.  If a TDSP owned meter is installed and the Customer still wants to have a competitively owned meter installed, follow the process beginning at Section 7.1(3).

## Notification Requirements

The notification requirements for a competitively owned meter installation are outlined below:

- Texas Meter Information (TMI) Form

- The TMI Form is used to request site specific parameters and specifications for competitive meter ownership.

- The Customer or Customer’s agent shall initiate the TMI Form.  The Customer or Customer’s agent is responsible for completing the “Contact Information” section of the TMI Form and sending the completed form to the TDSP, via e-mail.

- The TDSP shall return via email the completed TMI Form, to the initiating party within ten (10) Business Days of the date/time stamp on the senders e-mail.

- Agreement for Meter Ownership and/or Access

- The Agreement is executed by the Customer and the TDSP.  The Agreement is initiated by the Customer or Customer's agent and mailed to the TDSP. Upon execution by the TDSP, the Agreement will be returned to the Customer or Customer’s agent for their records.

- To be reviewed by COMET:

- Alternate language proposed for the initial sentence in section a:, if this supports the Agreement when finalized:

- The Customer and the TDSP execute the Agreement with the Meter Owner and/or Meter Access Agent acknowledging the agreement.

- The Customer, Customer's agent and meter owner, as applicable, and the TDSP will be responsible for completing the Agreement and providing the appropriate signatures where required.

- Need to revisit when the Agreement is finalized.

- Meter Test Results/Removal (MTR) Form

- The MTR Form is submitted, via e-mail, to the Customer or Customer’s agent, in the event the initial meter test results are unacceptable (failed).

- Texas Meter Access (TMA) Form

- The TMA Form is used to allow the Customer or Customer’s agent meter access following installation of a competitively owned meter.  This form may also be used to grant access to a TDSP owned meter. Release of this information requires completion of the “Data Access” section of the executed Agreement between the Customer and the TDSP.

- The TMA Form is completed by the TDSP and e-mailed to the Customer or Customer’s agent, if applicable, within ten (10) Business Days following the successful installation of a competitively owned meter.  The TMA Form provides site-specific parameters, which may include read-only passwords and communication information.

- For a TDSP owned meter, the Customer or Customer's agent may submit the TMA Form, via e-mail, to the TDSP, requesting site specific parameters, which may include read-only passwords and communication information.

## One ESI ID with Multiple Meters

If a Customer’s ESI ID involves the use of multiple meters and the Customer chooses to have one or more meters competitively owned at that ESI ID, then the number of meters that must be competitively owned and the associated meter credit for the ESI ID shall be based on the TDSP tariffs.

# Meter Testing and Calibration

## Accuracy Limits

At a minimum, meters shall comply with the test calibration limits set by the American National Standards Institute (ANSI). In addition, where a TDSP has established more stringent accuracy limits within their service territory, all meters shall comply with these accuracy limits. Whenever a meter is tested and found to be outside these TDSP accuracy limits, it shall be adjusted or replaced.

## Test Schedules

The test schedule for all types of in-service meters shall conform to the latest edition of ANSI Standard C12.  Within each TDSP service territory, meter test schedules have been established to ensure that all meters adhere to these standards.  All competitively owned meters will adhere to the test schedule for in-service meters of the TDSP service territory where they are installed.

## Meter Records

### Meter equipment record

Each TDSP shall keep a record of all competitively owned meters in its service territory, maintaining the Customer and meter owner’s contact information.

### Records of meter tests

Test records for a competitively owned meter shall be maintained by the TDSP, according to PUCT Substantive rules.

## TDSP Calibration

If a competitively owned meter is found to be outside the TDSP accuracy limits, the TDSP will attempt to calibrate the meter.

If the TDSP calibrates the meter, it shall be adjusted as closely as practicable to the condition of zero error.

If the TDSP is unable to calibrate the meter within accuracy limits, the TDSP will remove the meter, replace it with a properly functioning TDSP meter, and return the competitively owned meter as detailed in the Agreement.

## Notification Requirements

Upon request of a meter test for an in-service competitively owned meter, the TDSP will send the meter test results to the requestor and the CR.

# Removal of a Competitively Owned Meter

## Removal Requests to the TDSP

The TDSP will remove a competitively owned meter:

- Upon request by the Customer or Customer’s agent, via e-mail, for an energized service.

- Upon request via e-mail by the Meter Owner for a de-energized service.

Should there be an agreement directly with the meter owner and the TDSP?

## Removal Prior to Energization

The TDSP shall remove a competitively owned meter when it receives a request to energize a service unless the TDSP has received a newly executed Agreement between the new Customer and the Meter Owner, for that specific meter.

## Replacing Defective Equipment

- The TDSP will remove any meter found to be unsafe, defective, or damaged.

- The TDSP will remove any meter that fails to meet TDSP accuracy limits and the TDSP is unable to calibrate.

- The TDSP shall install a replacement TDSP owned meter capable of providing the data necessary for TDSP billing and for settlement.

- The defective or damaged competitively owned meter will be returned to the meter owner, according to the terms stated in the signed Agreement.

## Notification Requirements

It is the responsibility of the TDSP to notify the Customer and meter owner of the reason for removal of a competitively owned meter.

- The MTR Form will be e-mailed to the Customer and meter owner providing meter removal information.

- The TDSP will update ERCOT and the CR with the 814_20 SET ESI ID Maintenance transaction.

## Customer Requests to Return to TDSP Owned Meter

- The Customer or Customer’s agent may request to have a competitively owned meter removed and a TDSP owned meter installed.

The question that needs to be answered:

What are the TDSP obligations for monitoring a request to remove or replace a competitively owned meter with a TDSP owned meter?

Discussion:

Will the PUCT determine the rights of the Customer and meter owner to remove a meter?  The Tariff for Retail Delivery Service has determined the rights but the Agreement may further define processes.

Can the TDSP remove the meter if only the Customer requests removal but the meter owner wants the meter to remain?  PUCT staff opinion to this is yes.

Can the TDSP remove the meter if only the meter owner wants the meter removed but the Customer wants the meter to remain? Agreement will answer this.

Can the TDSP remove a competitively owned meter with a CR request if the CR is requesting the installation of an advanced meter? PUCT staff opinion on this is no.

Can the TDSP remove a competitively owned meter with a CR request if the CR is requesting the installation of an IDR meter per Protocol requirements?   CR will contact the Customer to coordinate the installation of an IDR meter if the Customer has a competitively owned meter installed.

## Safeguarding Meters

- Upon removal of a competitively owned meter, the TDSP shall take reasonable measures to safeguard the meter.

- Until the earlier of (a) the date the Meter Owner takes possession of the meter, or (b) 60 calendar days from the date of removal of the meter.

- If the Meter Owner fails to take possession of the meter within sixty (60) calendar days or upon thirty (30) days of the return of the meter that was shipped cash on delivery (COD), the TDSP is no longer responsible for safeguarding the meter and may dispose of it in any manner the TDSP deems appropriate.

Returning Meters

The TDSP may ship the competitively owned meter COD to the to the designated meter owner, according to the terms of the Agreement.

This section needs to be reviewed upon finalization of the Agreement.

- Customer or Third Party Access to the Meter

## Data Access

The Customer or Customer’s agent shall have the right to access meter data related to the Premise occupied by that Customer.

## Passwords

### Programming Passwords for TDSP Billing and Settlement Determinants

The TDSP has sole responsibility for maintaining the meter programming password that can be used to alter any TDSP billing and settlement determinants. No entity other than the TDSP shall have the right, capability, or meter programming password to alter the data collected by the meter for the purpose of TDSP billing.

### Programming Passwords for non-TDSP Billing and Settlement Determinants

A Customer or Customer’s agent owning a meter with security features that support multiple programming passwords is allowed access to programming passwords only if they do not allow alteration of TDSP billing and settlement determinants and/or data. Upon the execution of the “Access” section of the Agreement with the TDSP, the Customer or Customer’s agent shall be provided the non-billing parameter password for access and programming of meter data.

If the existing meter at the Premise is programmed for Supervisory Control and Data Acquisition (SCADA) related non-billing determinants which are being used by the TDSP for the safety and reliability of the TDSP transmission and/or distribution system, then the customer or customer’s agent shall not be allowed programming access to those determinants.

### Read-Only Passwords

Upon execution of the “Access” section of the Agreement with the TDSP, the Customer or Customer’s agent shall be provided read-only passwords for access to meter data.

## Meter Communication Responsibilities

Meter communication responsibilities shall be as defined in the “Access” section of the Agreement.

Need to verify this language upon approval of the Agreement.

## Physical Access

The current Customer or the Customer’s agent shall have the right to physical access to the meter to obtain meter data as long as the access is technically feasible and does not compromise the integrity of the metered data.

To facilitate safe physical access to the meter, the TDSP shall ensure that the requested physical connections to the meter are made available for external connections.

The TDSP shall terminate the physical connections to a point facilitating the Customer’s physical interface.

The Customer or the Customer’s agent shall be responsible for the installation and maintenance of all wiring and equipment on the Customer’s side of the point of interconnection.

Meter connections through which meter information can be exchanged include but are not limited to the meter display, digital pulse outputs, serial port, optical port, modem, network interface, power-line carrier, wireless, or pager interface

# TDSP billing and Credits per TDSP Approved Tariff

## TDSP Approved Credits

The TDSP is required to provide a competitive metering service credit to the CR for the ESI ID with a competitively owned meter installed. Information concerning the meter ownership credit can be found in each TDSP’s tariff.

## TDSP Approved Metering Service Credits and Tariffs

The approved discretionary service charges and competitive metering service credit information for each TDSP can be found on the PUCT website under electric rates and tariffs.

# Technical Specifications for Competitively Owned Meters

## Purpose

The purpose of this section is to provide minimum acceptable requirements and guidelines for competitively owned meters operating in areas where metering services are competitive.  These specifications shall apply to the meter functionality requested for approval.

## ANSI Standards

All electromechanical meters shall comply with the latest revision of the following applicable standards: ANSI C12.1, C12.4, C12.5, and C12.10.

All solid-state meters shall comply with the latest revision of the following applicable standards: ANSI C12.1, C12.10 and C12.20.

All meters approved prior to January 1, 2006 as to manufacturer’s type, are grandfathered from compliance with ANSI C12.18, C12.19, & C12.21.  In addition, a change in firmware does not require grandfathered meters to become compliant with these three standards. All meters, approved on or after January 1, 2006 shall comply with ANSI C12.18-2002, C12.19-1997, & C12.21-1999, if applicable.  C12.19 compliance includes accurate and complete documentation in Table 00.  At a minimum, Table 00 shall include Table 23, 27, 28 for all meters and Table 64 for load profile meters.  The tables are defined as follows:

Table 00 – General Configuration Table

Table 23 – Current Register Data Table

Table 27 – Present Register Selection Table

Table 28 – Present Register Data Table

Table 64 – Load Profile Data Set 1 Table

## TDSP Billing Determinants

The meter shall be capable of accurately measuring TDSP billing and settlement determinants.  For example, these determinants may include the following measurements: kW, kWh delivered and received, kVAR, kVARh delivered and received, power factor, Time of Use (TOU), and kVA–thermal (emulation arithmetic) as applicable. Meters may be approved based on manufacturer’s stated functionality after all required testing and approval processes are complete.

## Transformer and Line Loss Compensation – Optional Functionality

When transformer or line loss compensation is required, the meter shall perform this calculation in accordance with the latest revision of the “Handbook for Electricity Metering.” The meter shall be capable of accuracy testing both with and without Transformer Loss Compensation (TLC) factors applied.

The meter shall be programmable to display and record compensated values such as kW, kWh, kVAR and kVARh.

## Display

All meter displays shall meet the requirements of ANSI C12.10.  In addition, a solid state meter shall be capable of the following display functionality:

- Annunciators for all displayable energy units by name and code;

- Annunciators for all displayable non-energy units by code;

- Programmable scroll rate for displayed quantities ;

- Disk emulator with load flow indication;

- End of interval (EOI) indicator;

- Mode indicator (normal, alternate and test);

- A minimum of six digits, for energy units with a minimum resolution of  0.01; and,

- Active phase voltage indicators (applies to poly-phase meters only).

## Meter Diagnostics for Solid State Poly-phase Meters

Meter shall have installation diagnostic tools capable of performing and reporting all system service tests, including but not limited to the following:

- Per phase voltage

- Phase angle between voltage and current

- Per phase currents

- Voltage phase angle for validation of service configuration

## Solid State Display Modes

The following solid state display modes shall be selectable either by software or by an external switch.

### Normal Mode

The normal mode shall be capable of scrolling through all quantities and displayable items.

The normal mode shall be the default mode unless switched to another mode via software or by external switch.

### Alternate Mode

The alternate mode shall be capable of scrolling through all quantities and displayable items.

### Test Mode

The meter shall have the capability of a test mode function that suspends normal metering operation during testing so that additional consumption and demand from tests are not added to the meter’s normal mode display registers and the interval data.

Security shall be provided to prevent unauthorized access to the test mode.

Activation of the test mode shall cause all present critical TDSP billing data to be stored in non-volatile memory and restored at the time of exit from the test mode.

The meter shall be programmable to automatically exit the test mode and return to normal operation after one hour or less of operator inactivity.

The test mode shall have programmable displays.

## Power-up Operation

Upon power-up, the meter display shall operate in the normal mode and start to calculate consumption and demand quantities within ten (10) seconds.

Meter shall be programmable to permit a delay in the measurement of demand after a power failure. The delay shall be programmable for a period of anywhere from 0 to 60 minutes.

## Nameplate and Identifiers

### Nameplate

The meter shall be equipped with a nameplate as specified in the latest revision of ANSI C12.10 Standard.

The label “competitive meter” shall be placed in the space provided for the “utility name.”

### Internal Identifier

A solid state meter shall have the manufacturer’s serial number programmed internal to the meter.

## Self-Test

The meter shall be capable of performing a self-test to ensure that the meter is functioning properly and to verify data integrity.  As a minimum, the self-test shall be performed at the following times:

- After a power-up; and,

- Once per day.

## Diagnostic Checks

Upon failure of a diagnostic check, the meter shall store a status flag (indicator) that can be retrieved from the display or remotely, if applicable.  As a minimum, the following diagnostic checks shall be performed during a self-test:

- Check the backup battery usage or voltage;

- Verify the program configuration; and,

- Verify the memory integrity.

## IDR Pulse Overrun

The meter shall be capable of detecting and flagging if the maximum pulses per interval for the IDR have been exceeded for each interval.

## Event Logging

When interrogated, meters shall be capable of flagging and reporting the following events:

- Hardware errors;

- Firmware errors;

- RAM and ROM errors;

- Clock errors (timekeeping);

- Pulse Overflow errors;

- Low battery condition;

- AC power up;

- AC power down;

- Cold start (reinitialize all data to manufacturer’s default parameters);

- Warm start (initialize register data without changing program parameters);

- Configuration changed;

- Clock set/change;

- Test mode activation; and,

- Inactive potential.

## Error Reset

Error and warning conditions shall be programmable for display and reset, unless the manufacturer classifies the error as a fatal error.  Fatal errors shall only be reset upon an explicit command invoked via the meter programmer or upon some other explicit action.

## Communication

Communication requests from a single source or simultaneously from multiple sources shall not result in a meter malfunction, such as a measurement error, a meter lockup or loss of data.

### Local Communications Interface

The meter shall be capable of communicating with a personal computer through a local port.

### Internal Modem

Internal modems shall be capable of telephone communications at a minimum rate of 1200 baud.

The modem shall include baud select, configurable answer time window and configurable answer ring counter.

## Accuracy Standard

### Full Load, Light Load, & Power Factor

- Poly-phase solid state meters shall fully comply with ANSI C12.20, accuracy class 0.2. Form numbers not covered by this standard shall meet the accuracy requirements of ANSI C12.20, accuracy class 0.2.

- Single-phase solid state meters shall fully comply with C12.20, accuracy class 0.5, at a minimum. Form numbers not covered by this standard shall meet the accuracy requirements of ANSI C12.20, accuracy class 0.5.

- Upon receipt by the TDSP, the error for electromechanical meters shall be no greater than the following tolerances: Full Load: 0.4%, Light Load: 0.5%, Power Factor: 0.7%; Balance Test: 0.5%.

## Interval Data Recorder (IDR) Functionality

Meters with an IDR shall have the following interval data recording functions:

- Recording of interval data for a minimum of two (2) channels;

- Programmable intervals of five, fifteen, thirty, and sixty minutes;

- Ability to store date and time with the interval data;

- Storage of interval data for a minimum of forty-five (45) days per channel, fifteen (15) minute interval data, in addition to allowances for event recording (power outages, resets, time sets, etc.);

- Capacity to count and store at least 4,000 counts for the programmed interval for meters that store pulse data;

- “Wraparound” memory that stores new interval data by writing over the oldest interval data; and,

- Capability to continually record interval data while the meter is communicating via its communication ports.

## Internal Clock

The clock internal to the meter shall be accurate within two minutes per week (+/- 0.02%) when not synchronized to the line frequency and shall be re-settable through the communications interface utilizing the proper password security.

The meter shall be programmable to derive its time base from either the line frequency or the meter’s internal oscillator.

The meter shall be equipped with a software selectable Daylight Savings Time (DST) function.

## Outage Carryover

The meter data and time keeping functions shall have a minimum carry over time of 24 months without external power.

The meter configuration parameters as well as measured quantities for settlement determinants, excluding IDR data, shall be stored in non-volatile memory.

## Meter Password

The meter shall be programmable with a minimum of three (3) unique levels of password protection.  These levels are defined as follows:

- A first level allowing read only access of the meter data (to prevent unauthorized tampering by use of the optical port or the modem).

- A second level allowing read access with limited write access to meter functions (demand reset, time set, etc.).

- A third level allowing full programming access of all meter parameters.

## Reliability

Programming (except re-initialization), time synchronization, and reading shall not result in a meter malfunction, such as a measurement error, a meter lockup or loss of data.

## Field Requirements

### Field Testing

The meter shall provide a method to perform field accuracy testing using either infrared, LED, KYZ, disk emulation, or other industry-accepted method(s).

### Field Load Checks

The meter shall have the ability of displaying load rate, disk emulation or instantaneous values for measured quantities.

## Shop Requirements

Meters shall be compatible with existing commercial test boards that are available without modification for accuracy testing, using infrared, KYZ, LED, disk emulation, or other industry accepted method(s).

# Meter Approval Process

The following process shall be used for approving new meters to be added to the Qualified Competitive Meter List.

- A new meter is requested for a specific Customer’s location.

- An application is filed by the Customer and/or the Customer’s meter representative to competitivemetering@ercot.com which shall include:

- An ERCOT Meter Approval Application Form;

- Certification of compliance with applicable ANSI standards and the Technical Specifications for Competitively Owned Meters in these CMG;

- Meter Manufacturer’s ANSI Standards Test and meter test requirements data for the Technical Specifications for Competitively Owned Meters in these CMG;

- A letter from the meter manufacturer indicating that the manufacturer will supply programming software and adequate training to the TDSP at no charge, within thirty (30) calendar days of receipt of the meter(s).  Adequate training may be supported via on-site visit, telephone call, software/video recording, web-based or other agreed upon means between the manufacturer and each TDSP.  Software provided will be capable of retrieving TDSP billing and settlement data directly from the meter in a recognized industry standard readable format in case of communication failure; and,

- Detailed meter information document including settlement functionality.

- ERCOT reviews the application for completeness, and to determine if information to demonstrate ANSI compliance has been submitted.

- If needed ERCOT requests more information.

- After receipt of all information, ERCOT shall accept or reject the application within thirty (30) calendar days or notify the applicant of the status of the application.

- If the application is accepted, ERCOT forwards the application along with notification that the manufacturer’s test data is available to each TDSP.

- If the application is rejected, ERCOT returns the application to the Customer and/or Customer’s representative with specific reason(s) for the rejection.

- Upon acceptance of the application, ERCOT posts notice on the ERCOT website that the meter is under review for approval.

- TDSPs will review the manufacturer’s test data and may test the meter using applicable standards and share data with other TDSPs and ERCOT.

- Each TDSP will decide if they require additional tests.

- TDSPs may request a meter, software and training from the manufacturer.

- Any TDSP choosing to test the meter must do so within thirty (30) calendar days or notify the applicant of the status of the additional tests.

- Any TDSP choosing to test the meter shall send the meter test results, data and conclusions to other TDSPs and ERCOT.

- The TDSPs and ERCOT shall jointly review the test results.

- If requested, ERCOT will make information available to other Market Participants, to the extent that the information owner does not mark such information as Protected Information.

- ERCOT approves the application based on a positive recommendation by a minimum of 80% of the TDSPs; otherwise the application is rejected and ERCOT removes the notice that the meter is under review for approval from the ERCOT web site.

- If the application is approved, the meter is added to the Qualified Competitive Meter List.

    - ERCOT informs the applicant of the approval.

    - ERCOT updates the Qualified Competitive Meter List.

    - ERCOT posts the new list with the effective date.

- If the application is rejected, ERCOT will provide documentation to the applicant of the specific reason(s) for rejection, based on identifiable deviation from the applicable Technical Specifications for Competitively Owned Meters as documented in these CMG.

- Any subsequent application for approval of a rejected meter must include the manufacturer’s documented resolution of the reason for the previous rejection.

# Meter Firmware/Functionality Changes for an Approved Meter

The following process shall be used for approving changes to meter firmware or functionality for meters currently on the Qualified Competitive Meter List:

- Meter manufacturer, Customer and/or the Customer’s meter representative requests the addition of a firmware number and/or an upgrade in functionality for a meter that is currently in approved status on the Qualified Competitive Meter List and the meter programming software previously provided by the manufacturer is still applicable.

- Application may be filed by the meter manufacturer, Customer and/or the Customer’s meter representative to competitivemetering@ercot.com which shall include:

- An ERCOT Meter Firmware/Functionality Upgrade Approval Application Form;

- A detailed listing of the changes made and/or the reason for the upgrade;

- Certification of compliance with applicable ANSI standards and the Technical Specifications for Competitively Owned Meters detailed in these CMG, if applicable; and,

- Meter Manufacturer’s ANSI Standards Test and meter test requirements data for the Technical Specifications for Competitively Owned Meters in these CMG, if applicable.

- ERCOT reviews the application for completeness, and to determine if information to demonstrate ANSI compliance has been submitted, if applicable.

- If needed ERCOT requests more information.

- After receipt of all information, ERCOT shall accept or reject the application within twenty (20) calendar days or notify the applicant of the status of the application.

- If the application is accepted, ERCOT forwards the application along with notification that the manufacturer’s test data is available to each TDSP.

- If the application is rejected, ERCOT returns the application to the applicant with specific reason(s) for the rejection.

- Upon acceptance of the application, ERCOT posts notice on the ERCOT website that the meter firmware number and/or functionality upgrade is under review for approval.

- TDSPs will review the manufacturer’s test data and may test the meter firmware/functionality using applicable standards and share the data with other TDSPs and ERCOT.

- Each TDSP will decide if they require additional tests.

- TDSPs may request a sample meter from the manufacturer for testing the firmware/functionality upgrade.

- Any TDSP choosing to test the meter firmware/functionality must do so within twenty (20) calendar days or notify the applicant of the status of the additional tests.

- Any TDSP choosing to test the meter firmware/functionality shall send the test results, data and conclusions to the other TDSPs and ERCOT.

- The TDSPs and ERCOT shall jointly review the test results.

- If requested, ERCOT will make information available to other Market Participants, to the extent that the information owner does not mark such information as Protected Information.

- ERCOT approves the application based on a positive recommendation by a minimum of 80% of the TDSPs; otherwise the application is rejected and ERCOT removes the notice that the meter firmware number and/or functionality upgrade is under review for approval from the ERCOT website.

- If the application is approved, the new meter firmware number and/or functionality is added to Qualified Competitive Meter List.

    - ERCOT informs the applicant of the approval.

    - ERCOT updates the Qualified Competitive Meter List.

    - ERCOT posts the new list with the effective date.

- If the application is rejected, ERCOT will provide documentation to the applicant of the specific reason(s) for rejection, based on identifiable deviation from the applicable Technical Specifications for Competitively Owned Meters as documented in these CMG.

- Any subsequent application for approval of a rejected firmware/functionality upgrade must include the manufacturer’s documented resolution of the reason for the previous rejection.

# Meter Issue Resolution Process

The following process shall be used to resolve issues involving non-compliance with ERCOT approved competitive meter standards, for meters on the Qualified Competitive Meter List:

- TDSP notifies the manufacturer of product issue and requests a written response.

- The TDSP shall notify ERCOT, via e-mail, utilizing the Meter Issue Resolution Form and include the manufacturer’s written response to the issue.

- ERCOT reviews the issue.

- ERCOT verifies that the TDSP meter issue is supported based on the documentation received.

- ERCOT may request clarification from the TDSP and/or the manufacturer.

- ERCOT confirms that there is a non-compliant product issue and enters the information on the Meter Issue Resolution Form.

- ERCOT sends a notification, including the supporting documentation, to each TDSP, and to the meter manufacturer, if issue is confirmed.

- In order to remain on the Qualified Competitive Meter List, the manufacturer must resolve the issue with the TDSPs and ERCOT.

- TDSPs and ERCOT unanimously determine if new installations must be placed on hold due to safety and/or impacts on TDSP billing and settlement determinants.

- If a meter is placed on hold, ERCOT will update the status of the meter on the Qualified Competitive Meter List.

- If the manufacturer requests more time to resolve the issue, the TDSPs and ERCOT set the timeline for the issue resolution.

- The manufacturer provides the resolution to ERCOT who then forwards the documentation to all TDSPs.

- TDSPs and ERCOT unanimously determine if the issue is resolved, and the hold is removed, if applicable.

- If the issue is not resolved, ERCOT updates the Meter Issue Resolution Form based on a unanimous recommendation by the TDSPs.

- ERCOT receives the documentation from the TDSPs and attaches the manufacturer’s response.

- ERCOT posts notification to the ERCOT website that the approved meter functionality/restrictions/firmware will be changed or the meter will be removed from the Qualified Competitive Meter List.

- TDSPs send notification to the Customer or the Customer’s agent that the meter will be removed from service.

- ERCOT updates the Qualified Competitive Meter List including an effective date.

# Meter Ownership Transfer

## Introduction

If a meter ownership transfer occurs, the Customer must execute a new Agreement with the TDSP indicating the new owner.

This section will need to be reviewed upon finalizing the agreement and finalizing the rights of the Customer’s agent and a third party meter owner.

## Communication Process

The Customer is responsible for providing all the required contact and meter return information for the new meter owner, along with the appropriate authorized signatures to the TDSP.

The TDSP will have fifteen (15) Business Days to process the Agreement and return the executed Agreement to the Customer.

This section will need to be reviewed upon finalizing the agreement and finalizing the rights of the Customer’s agent and a third party meter owner.

The TDSP will e-mail confirmation to the new meter owner, within five (5) business days of the ownership transfer that the ownership transfer request has been completed.

The TDSP will be responsible for updating their internal records for ownership type and modifying the 814_20 Meter Owner Type code, if applicable.

# Competitive Metering Guides Change Control Process

## Overview

The following process has been established to announce, develop, revise, and approve changes to the Competitive Metering Guides (CMG):

- Proposed CMG revisions are submitted to ERCOT at competitivemetering@ercot.com.

- The Competitive Metering Working Group (COMETWG) reviews the Competitive Metering Guides Revision Request (CMGRR) and recommends an action to the Retail Market Subcommittee (RMS).

- After reviewing the COMETWG’s recommendation to revise the CMG, the RMS approves or rejects the recommendation.

- Upon approval, RMS submits proposed CMG language revisions to the Technical Advisory Committee (TAC) for review and approval.

- The TAC reports the results of all TAC votes regarding proposed CMG revisions to the ERCOT Board of Directors.

Throughout the CMG, references are made to the Protocols.  Protocols are subject to their own revision process, not this CMG revision process.

## Roles and Responsibilities

### Market Participant

Any Market Participant may submit a CMGRR. The Market Participant is responsible for monitoring the progress of their submittal. Submitters are encouraged to attend COMETWG meetings and offer suggested language that ensures the intent of the request is maintained.

### COMETWG

The COMETWG has ultimate responsibility for ensuring that the CMG are compliant with Protocols.  As such, the COMETWG will monitor all changes to Protocols and initiate any CMGRRs necessary to bring the CMG into conformity with Protocols.

The COMETWG will acknowledge receipt of all CMGRRs it receives.  The COMETWG will also provide progress updates to the submitter of the CMGRR apprising the submitter of the status of the CMGRR at each major step of the approval process.  All communication between the submitter of a CMGRR and the COMETWG will be done using electronic mail.

### ERCOT

When ERCOT is assigned duties in the Change Control Process the ERCOT Settlement Metering Department will be responsible for performing the work.

ERCOT will have the responsibility for managing the process used to track submitted changes to the Competitive Metering Guides.

Step by Step Process

| CHANGE CONTROL PROCESS |  |
| --- | --- |
| STEP | PROCESS |
| 1. Request to Revise Competitive Metering Guides | Requests to revise the CMG are submitted electronically to ERCOT utilizing the designated CMGRR form. Any Entity with a legitimate interest in competitive metering may offer a pertinent revision for consideration. These Entities include, but are not limited to: - Transmission and Distribution Service Providers - Competitive Retailers - Load Serving Entities - Power Marketers - Qualified Scheduling Entities - ERCOT Subcommittees, Task Forces, and Working Groups - ERCOT - Non Opt In Entities - PUCT The original submission of a CMGRR must be accompanied by a description of the requested revision, the reason for the suggested revision, a list of any other affected ERCOT Guides sections, and the suggested CMG language. A CMGRR is first submitted to ERCOT where the request is verified for completeness. Within five Business Days, ERCOT will notify the submitter that the CMGRR has been received. At this time ERCOT will also inform the submitter whether the CMGRR is considered complete or not complete. Completed CMGRRs are forwarded to the COMETWG for review. CMGRRs that are not complete are returned to the submitter. No further action will be taken by ERCOT on any CMGRR deemed incomplete. To pursue the request further, the submitter must submit a new CMGRR. ERCOT will use the Competitive Metering Exploder list to forward the CMGRR to the Chair of the COMETWG. The Chair will place this CMGRR on the agenda for the next regularly scheduled COMETWG meeting. If the next regularly scheduled COMETWG meeting will occur more than 30 days after a CMGRR is submitted to ERCOT, the Chair of the COMETWG may convene a special meeting of the COMETWG to discuss this request. |
| 2. Competitive Metering Working Group Reviews Request and Recommends Action | As part of the CMGRR evaluation process, the COMETWG will establish a timetable for completing its review and analysis of the submitted CMGRR. The COMETWG will provide a recommended implementation date for any CMG language forwarded to the RMS for review and approval. The COMETWG will be responsible for verifying the accuracy of all information contained in a submitted CMGRR. The COMETWG will also be responsible for researching the impacts to other Operating Guides when making this CMG language revision. Further, the COMETWG will be responsible for ascertaining that the proposed CMG language revision complies with Protocols. The COMETWG will sponsor changes to the Protocols when these changes must be made to accommodate the proposed CMG language revisions. During the process of evaluating a CMGRR, the COMETWG may circulate the proposal to other working groups for review and comment. The COMETWG shall have no responsibility to address or incorporate comments from the other working groups into its CMG language revisions. After the COMETWG reviews the CMGRR one of three actions will be taken: - The CMGRR is accepted as submitted and the CMG language revisions are forwarded to the RMS for approval, or - The CMGRR is accepted with COMETWG modifications and the resulting CMG language revisions are submitted to the RMS for approval, or - The CMGRR is rejected. Action 1. When the COMETWG accepts a CMGRR as submitted, the COMETWG will forward the proposed CMG language revisions to the RMS for review and approval at the next regularly scheduled meeting of the RMS. Action 2. When the COMETWG accepts the CMGRR in principle, but has concerns with some elements of the CMGRR, the COMETWG will draft alternative proposed CMG language. The revised CMG language will be submitted to the RMS for review and approval at the next regularly scheduled meeting of the RMS. The COMETWG will inform the Entity submitting the CMGRR that the COMETWG will forward the CMG language revisions to the RMS for review and approval; however the COMETWG has modified the submitter’s proposed CMG language revisions to better reflect the viewpoint of the COMETWG. The submitter may forward its original CMGRR to the RMS for consideration as an alternative to the CMG language revisions submitted by the COMETWG. Action 3. When the COMETWG rejects a CMGRR the COMETWG will issue a report to the submitter of the CMGRR within five Business Days of the COMETWG making its determination. This report will include the original CMGRR and a detailed reason for the rejection decision. A submitter has ten Business Days to register a request to appeal the decision of the COMETWG with the RMS. |
| 3. Retail Market Subcommittee Reviews and Comments on Recommendation to Revise Guides Language | When the RMS reviews the proposed CMG language revisions one of four actions will be taken: - The proposed CMG language revisions are approved as submitted, or - The proposed CMG language revisions are conditionally approved for submittal to the TAC, or - The proposed CMG language revisions are sent back to the COMETWG for further work, or - The proposed CMG language revisions are rejected. Action 1. When the RMS approves the proposed CMG language revisions as presented, the RMS will submit the proposed CMG language revisions to TAC for review and approval. Action 2. When the RMS accepts the proposed CMG language revisions, but requests the COMETWG make specific changes to the language before having it submitted to the TAC, the COMETWG could accept or reject the language edits offered by the RMS. If the COMETWG accepts the language edits offered by the RMS then the CMG language revisions are forwarded to the TAC for review and approval. If the COMETWG rejects the language edits made by the RMS then CMG language revisions are treated as though the RMS sent it back to the COMETWG for further work. Follow the steps for Action 3. Action 3. When the RMS accepts the proposed Guides language revisions in concept, but has concerns with some of the details, the RMS will return the proposed CMG language revisions to the COMETWG with comments and a request for additional COMETWG work on this proposal. The COMETWG can take one of two further actions: - Discontinue further action toward implementing the proposed CMG language revisions, or - Modify the proposed CMG language revisions to accommodate concerns of the RMS. Further Action 1. When, after taking into consideration the review and commentary of the RMS, the COMETWG determines that the proposed Guides language is not necessary, a response will be prepared stating why the proposed Guides language revisions are no longer being pursued by the COMETWG. This response will be sent to the Chair of the RMS, and to the submitter of the original CMGRR. Further Action 2. After the proposed CMG language revisions have been modified to accommodate concerns raised by the RMS, the Chair of the COMETWG will submit the modified proposed CMG language revisions to the RMS for review and approval. Action 4. When the RMS decides not to approve the proposed CMG language revisions, the RMS will provide the COMETWG with reasons why the RMS rejected the proposed CMG language revisions. - At this point the COMETWG can pursue one of two further actions: Discontinue further action toward implementing the proposed CMG language revisions, or - Resubmit the proposed CMG language revisions to the RMS after reworking it to address the objections of the RMS. Further Action 1. When the COMETWG accepts the decision of the RMS, then a response to the submitter of the CMGRR is prepared by the COMETWG stating that the COMETWG will take no further action concerning the CMGRR. This communication will state that the RMS rejected the proposed CMG language revisions suggested in the CMGRR. This communication will also state the reasons why the RMS rejected the proposed CMG language revisions. Further Action 2. When the COMETWG determines that the proposed CMG language revisions should be adopted, the COMETWG will develop proposed CMG language revisions that address the objections raised by the RMS during this Subcommittee’s initial review of the proposed CMG language revisions. The revised CMG language revisions will be resubmitted to the RMS for review at the next regularly scheduled meeting of the RMS. Step three of this process begins anew. |
| 4. Technical Advisory Committee Reviews the Proposed Guides Language Revisions | The TAC will review the proposed Guides Language revisions at its next regularly scheduled meeting where one of three actions will occur: - The proposed CMG language revisions are approved as submitted, or - The proposed CMG language revisions are sent back to the COMETWG for additional work. - The proposed CMG language revisions are rejected. Action 1. If the TAC approves the proposed CMG language revisions, the revisions will have an effective date occurring on the first day of the month following TAC approval unless otherwise designated by the COMETWG. Action 2. If the TAC determines that the proposed CMG language revisions need further work, then the request will be sent back to the COMETWG to address TAC’s issues. Unless otherwise directed, the resulting modified CMG language must pass through the RMS review and approval process described in Step 3 above. Action 3. If TAC rejects the proposed CMG language revisions, the COMETWG will terminate any further activity toward implementing these proposed CMG language revisions. Within three Business Days of TAC making its decision, the COMETWG will notify the Entity submitting the CMGRR of TAC’s decision to reject the proposed CMG language revisions as suggested in the CMGRR. |
| 5. Technical Advisory Committee notifies the ERCOT Board of all votes taken related to Guides Revisions | The Chair of TAC shall report the results of all votes by TAC related to the CMG language revisions to the ERCOT Board at their next regularly scheduled meeting. |

# Metering Forms

## Forms Posted on the ERCOT Web Site

The current version of these forms should be downloaded from the ERCOT Competitive Metering web page before submitting per the instructions in these CMG:

Go to www.ercot.com

Select the “Market Participants & Stakeholders” tab

Select “Competitive Metering”

- Texas Meter Information (TMI) Form;

- Texas Meter Access (TMA) Form;

- Meter Test Results / Meter Removal (MTR) Form;

- Meter Approval Application Form;

- Meter Functionality/Firmware Approval Application Form;

- Meter Issue Resolution Form;

- Competitive Metering Guides Revision Request; and,

- Agreement for Meter Ownership and/or Access.

## Form Revision

The COMETWG is responsible for making revisions to existing forms or creating new forms to meet the requirements of competitive meter ownership.